## Sheet1
table 6
IS Number | Part | Section | Year | Number of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause/ Table/ Annex Reference | Test Parameter Name | To be tested and/or reported by Lab (YES / NO) | Mandatory or Optional | Characteristics (as per Indian Standard) - No specified values to be mentioned here | Test Result/ Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference | Sample Quantity | Equipment | Remark | Nominal System Voltage Up to 1.1 kV, Phase-to-Phase Clearance in mm, Min | Nominal System Voltage Up to 1.1 kV, Phase-to-Phase Clearance in mm, Max | Nominal System Voltage Up to 1.1 kV, Phase-to-Earth Clearance in mm, Min | Nominal System Voltage Up to 1.1 kV, Phase-to-Earth Clearance in mm, Max | Nominal System Voltage 11 kV, Phase-to-Phase Clearance in mm, Min | Nominal System Voltage 11 kV, Phase-to-Phase Clearance in mm, Max | Nominal System Voltage 11 kV, Phase-to-Earth Clearance in mm, Min | Nominal System Voltage 11 kV, Phase-to-Earth Clearance in mm, Max | Nominal System Voltage 22 kV, Phase-to-Phase Clearance in mm, Min | Nominal System Voltage 22 kV, Phase-to-Phase Clearance in mm, Max | Nominal System Voltage 22 kV, Phase-to-Earth Clearance in mm, Min | Nominal System Voltage 22 kV, Phase-to-Earth Clearance in mm, Max | Nominal System Voltage 33 kV, Phase-to-Phase Clearance in mm, Min | Nominal System Voltage 33 kV, Phase-to-Phase Clearance in mm, Max | Nominal System Voltage 33 kV, Phase-to-Earth Clearance in mm, Min | Nominal System Voltage 33 kV, Phase-to-Earth Clearance in mm, Max | Rating 16 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 63 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 63 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 160 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 160 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 200 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 200 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 20250000 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 250 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 250 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 315 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 315 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 400 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 400 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 500 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 500 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 630 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 630 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 800 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 800 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1000 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1000 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1250 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1250 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 1600 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 1600 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 2000 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2000 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 2500 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 2500 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 1, Total Losses Upto 11kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 2, Total Losses Upto 11kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 3, Total Losses Upto 11kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 4, Total Losses Upto 11kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 5, Total Losses Upto 11kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 1, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 2, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 3, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 4, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 5, Total Losses above 11 kV and up to and including 22 kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 5 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 5 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 10 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 10 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 16 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 16 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 25 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 25 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 50 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 50 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 75 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 75 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 1, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 2, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 3, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 4, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max | Rating 100 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Min | Rating 100 KVA, Energy efficiency level 5, Total Losses above 22 kV and up to and including 33 kV Class Transformers (W), Max
THIS ROW TO BE LEFT BLANK
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV —Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 6.9.1, 7.9.1, 8.9.1 | Permissible Flux density and Over Fluxing | No | Mandatory | The maximum flux density in any part of the core and yoke at rated voltage and frequency shall be such that the flux density with +12.5 percent combined voltage and frequency variation from rated voltage and frequency does not exceed 1.9 Tesla. (Unit: Tesla) | (1 observation, Value up to 1 decimal place) | Name plate drawing , General Arrangement (GA) drawing; Flux density design calculation sheet; Core Coil Assembly drawing mention HV and LV conductor size are to be attached with this Test Request. |  |  | To be only filled if the Column I and Column J are having same information and Column M is having different information | NOT TO BE FILLED |  | Single Observation for each Flux density and Over Fluxing. The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 6.9.2, 7.9.2, 8.9.2 | Permissible Flux density and Over Fluxing | No | Mandatory | No-load current up to 200 kVA shall not exceed 3 percent of full load current and will be measured by energizing the transformer at rated voltage and frequency. (Unit: %) | (1 observation, Value up to 1 decimal place) | Name plate drawing , General Arrangement (GA) drawing; Flux density design calculation sheet; Core Coil Assembly drawing mention HV and LV conductor size are to be attached with this Test Request. | [5 empty] | Single Observation for each Clause rated voltage and frequency. The requirements shall be verified in the factory during preliminary inspection for ensuring conformity. The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 6.9.2, 7.9.2, 8.9.2 | Permissible Flux density and Over Fluxing | No | Mandatory | Increase of 12.5 percent of rated voltage shall not increase the no load current by 6 percent maximum of full load current. (Unit: %) | (1 observation, Value up to 1 decimal place) | Name plate drawing , General Arrangement (GA) drawing; Flux density design calculation sheet; Core Coil Assembly drawing mention HV and LV conductor size are to be attached with this Test Request. | [5 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 9.1 | Standard Materials | No | Mandatory | Major material used in the transformer shall conform to the following Indian Standards: | 5 observation, Value upto 1 decimal place | [6 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 9.1 a) | Standard Materials | No | Mandatory | Cold rolled grain oriented electrical steel | (5 observation, Value upto 1 decimal place) Please see the Test Report of IS 3024 | [6 empty] | Shall be ISI Marked with supplier test certificate. The requirements shall be verified in the factory during preliminary inspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 9.1 b) | Standard Materials | No | Mandatory | Amorphous core material | (5 observation, Value upto 1 decimal place) Please see the Test Report of IS 16585 | [6 empty] | Shall be ISI Marked with supplier test certificate.The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 9.1 c) | Standard Materials | No | Mandatory | Copper/Aluminum conductor | (5 observation, Value upto 1 decimal place) Please see the Test Report of – IS 191, IS 1897, IS 7404, IS 12444, IS 13730/IS 6162 series as given in Annex A of IS 1180 Part 1. | [6 empty] | Shall be ISI marked/ Test certificate of conformity to IS 191, IS 1897, IS 7404, IS 12444, IS 13730/IS 6162 series as given in Annex A of IS 1180 (Part 1). The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 9.1 d) | Standard Materials | No | Mandatory | Kraft paper | (5 observation, Value upto 1 decimal place) Please see the Test Report of – IS 9335 series as given in Annex A of IS 1180 Part 1. | [6 empty] | Shall be ISI Marked/ Test Certificate of Conformity to IS 9335 series as given in Annex A of IS 1180 (Part 1). The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 9.1 e) | Standard Materials | No | Mandatory | Press board | (5 observation, Value upto 1 decimal place) Please see the Test Report of IS 1576 | [6 empty] | Shall be ISI Marked/ Test Certificate of Conformity to IS 1576. The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 10.1.1 | Bushings | No | Mandatory | Bushings | (3 observation) Please see the Test Report of IS/IEC 60137 and IS- 7421 | [6 empty] | Shall be ISI Marked/ Test Certificate of Conformity to IS/IEC 60137 and IS 7421. The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 10.1.5 | Dimensions of Bushings | No | Mandatory | Dimensions of Bushings | (3 observation) Please see the Test Report of IS 3347 series as given in AnnexA of IS 1180 (Part 1), IS 8603, IS 8603-4, IS/IEC 60137, IS 7421 | [6 empty] | Shall be ISI Marked/ Test Certificate of Conformity to IS 3347 series as given in Annex A of IS 1180 (Part 1), IS 8603, IS 8603-4, IS/IEC 60137, IS 7421. The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 15.4 | Gasket | No | Mandatory | Gasket | (5 observation, Value upto 1 decimal) Please see the Test Report ofType III as per IS 11149/ Type C as per IS 4253 (Part 2) | [6 empty] | Shall be ISI Marked/ Test Certificate of Conformity to Type III as per IS 11149/ Type C as per IS 4253 (Part 2). The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 9.1 f) | Standard Materials | No | Mandatory | Mineral oil | Please see the Test Report of IS 335 | [6 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 11, Table 10 | Minimum clearances in air | No | Mandatory | The minimum phase-to-phase and phase-to-earth external clearances for LV and HV bushings shall be as per Table 10 (Unit: mm) | 1 observation | Nominal System Voltage | [5 empty] | Single observations for Minimum clearance in air. The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity. | 75 |  | 40 |  | 255 |  | 140 |  | 330 |  | 230 |  | 350 |  | 320
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 15.1.1 | Construction of Transformer Tank | No | Mandatory | For non-sealed or sealed type transformer, transformer tank can be of plain tank configuration with/without radiator fins or cooling tubes. The tank can also be made of corrugated panels of adequate thickness, also used for cooling. The transformer tank covers shall be bolted/clamped alternatively welded with tank rim so as to make a leak proof joint. The curb design in case of welded construction shall be such that it is possible to remove the weld and reweld the tank at least two times. | Satisfactory/Unsatisfactory | Name plate drawing , General Arrangement (GA) drawing; Flux density design calculation sheet; Core Coil Assembly drawing mention HV and LV conductor size are to be attached with this Test Request. | [5 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 15.1.2 | Construction of Transformer Tank | No | Mandatory | The transformer tank shall be of adequate mechanical strength to withstand positive and negative pressures built up inside the tank while the transformer is in operation. | Satisfactory/Unsatisfactory | Name plate drawing , General Arrangement (GA) drawing; Flux density design calculation sheet; Core Coil Assembly drawing mention HV and LV conductor size are to be attached with this Test Request. | [5 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 15.1.3 | Construction of Transformer Tank | No | Mandatory | All welding operations shall be carried out by qualified welders. | Satisfactory/Unsatisfactory | [6 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity. Qualification Certificate of the welder to be maintained
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 15.1.4 | Construction of Transformer Tank | No | Mandatory | The tank design shall be such that the core and windings can be lifted freely. | Satisfactory/Unsatisfactory | [6 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 15.1.5 | Construction of Transformer Tank | No | Mandatory | For single phase sealed type transformers, the circular base plate edges of the tank shall be folded upward for at least 25 mm, to have sufficient overlap with vertical sidewall of the transformer. (Unit: mm ) | 1 observation, Value upto 2 decimal places | [6 empty] | Single observation for Construction of Transformer Tank. The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 15.5, Table 12 | Painting of Transformer Tank | No | Mandatory | Inside of tank shall be painted with varnish or oil resistant paint. For external surfaces one coat of thermo setting powder paint or one coat of epoxy primer followed by two coats of polyurethane base paint shall be used. Table 12 shall be referred to for paint thickness for normal to medium corrosive atmosphere. For highly polluted atmosphere and special application external paint work shall be subject to agreement between the user and the transformer manufacturer. | Satisfactory/Unsatisfactory | [6 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 16.1 | Conservator for non- sealed type transformer | No | Mandatory | Transformers of ratings 63 kVA and above with plain tank construction, the provision of conservator is mandatory. For corrugated tank and sealed type transformers with or without inert gas cushion, conservator is not required. | Satisfactory/Unsatisfactory | [6 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 16.2 | Conservator for non- sealed type transformer | No | Mandatory | When a conservator is provided, oil gauge and the plain or dehydrating breathing device shall be fixed to the conservator which shall also be provided with a drain plug and a filling hole (1¼″ normal size thread) with cover. The capacity of a conservator tank shall be designed keeping in view the total quantity of oil and its contraction and expansion due to temperature variations. In addition, the cover of main tank shall be provided with an air release plug to enable air trapped within to be released, unless the conservator is so located as to eliminate the possibility of air being trapped within the main tank. | Satisfactory/Unsatisfactory | [6 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 16.3 | Conservator for non- sealed type transformer | No | Mandatory | The inside diameter of the pipe connecting the conservator to the main tank should be 25 to 50 mm (Unit: mm) | 3 observation, Value upto 1 decimal place | [6 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 16.3 | Conservator for non- sealed type transformer | No | Mandatory | and it should be projected into the conservator so that its end is at least 20 mm above the bottom of the conservator so as to create a sump for collection of impurities. (Unit: mm) | 3 observation, Value upto 1 decimal place | [6 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 16.3 | Conservator for non- sealed type transformer | No | Mandatory | The minimum oil level corresponding to–5°C should be above the sump level (Unit: °C) | 3 observation, Value upto 1 decimal place | [6 empty] | The requirements shall be verified in the factory during preliminaryinspection for ensuring conformity.
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 a) | Measurement of Winding Resistance | Yes | Mandatory | 10.2.1 General The resistance of each winding, the terminals between which it is measured and the temperature of the windings shall be recorded. Direct current shall be used for the measurement.In all resistance measurements, care shall be taken that the effects of self-induction are minimized. (Unit: ohm) | 9 observation; Value upto 1 decimal place |  | Cl.10.2 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of Winding Resistance
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 a) | Measurement of Winding Resistance | Yes | Mandatory | 10.2.2 Dry-Type Transformers, before measurement the transformer shall be at rest in a constant ambient temperature for at least 3h. Winding resistance and winding temperature shall be measured at the same time. The winding temperature shall be measured by sensors placed at representative positions, preferably inside the set of windings, for example, in a duct between the high-voltage and low-voltage windings. Before SCW test for HV winding resistance (Unit: ohm) | 9 observation; Value upto 1 decimal place |  | Cl.10.2 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of Winding Resistance
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 a) | Measurement of Winding Resistance | Yes | Mandatory | 10.2.2 Dry-Type Transformers, before measurement the transformer shall be at rest in a constant ambient temperature for at least 3h. Winding resistance and winding temperature shall be measured at the same time. The winding temperature shall be measured by sensors placed at representative positions, preferably inside the set of windings, for example, in a duct between the high-voltage and low-voltage windings. After SCW test for HV winding resistance (Unit: ohm) | 9 observation; Value upto 1 decimal place |  | Cl.10.2 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of Winding Resistance
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 a) | Measurement of Winding Resistance | Yes | Mandatory | 10.2.2 Dry-Type Transformers, before measurement the transformer shall be at rest in a constant ambient temperature for at least 3h. Winding resistance and winding temperature shall be measured at the same time. The winding temperature shall be measured by sensors placed at representative positions, preferably inside the set of windings, for example, in a duct between the high-voltage and low-voltage windings. Before SCW test for LV winding resistance (Unit: ohm) | 9 observation; Value upto 1 decimal place |  | Cl.10.2 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of Winding Resistance
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 a) | Measurement of Winding Resistance | Yes | Mandatory | 10.2.2 Dry-Type Transformers, before measurement the transformer shall be at rest in a constant ambient temperature for at least 3h. Winding resistance and winding temperature shall be measured at the same time. The winding temperature shall be measured by sensors placed at representative positions, preferably inside the set of windings, for example, in a duct between the high-voltage and low-voltage windings. After SCW test for LV winding resistance (Unit: ohm) | 9 observation; Value upto 1 decimal place |  | Cl.10.2 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of Winding Resistance
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 a) | Measurement of Winding Resistance | Yes | Mandatory | 10.2 Oil-Immersed Type Transformers , after the transformer has been under oil without excitation for atleast 3 h, the average oil temperature shall be determined and the temperature of the winding shall be deemed to be the same as the average oil temperature. The average oil temperature is taken as the mean of the top and bottom oil temperatures. In measuring the cold resistance for the purpose of temperature-rise determination, special efforts shall be made to determine the average winding temperature accurately. Thus, the difference in temperature between the top and bottom oil should be small. To obtain this result more rapidly, the oil may be circulated by a pump. Before SCW test for HV winding resistance (Unit: ohm) | 9 observation; Value upto 1 decimal place |  | Cl.10.2 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of Winding Resistance
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 a) | Measurement of Winding Resistance | Yes | Mandatory | 10.2 Oil-Immersed Type Transformers , after the transformer has been under oil without excitation for atleast 3 h, the average oil temperature shall be determined and the temperature of the winding shall be deemed to be the same as the average oil temperature. The average oil temperature is taken as the mean of the top and bottom oil temperatures. In measuring the cold resistance for the purpose of temperature-rise determination, special efforts shall be made to determine the average winding temperature accurately. Thus, the difference in temperature between the top and bottom oil should be small. To obtain this result more rapidly, the oil may be circulated by a pump. After SCW test for HV winding resistance (Unit: ohm) | 9 observation; Value upto 1 decimal place |  | Cl.10.2 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of Winding Resistance
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 a) | Measurement of Winding Resistance | Yes | Mandatory | 10.2 Oil-Immersed Type Transformers , after the transformer has been under oil without excitation for atleast 3 h, the average oil temperature shall be determined and the temperature of the winding shall be deemed to be the same as the average oil temperature. The average oil temperature is taken as the mean of the top and bottom oil temperatures. In measuring the cold resistance for the purpose of temperature-rise determination, special efforts shall be made to determine the average winding temperature accurately. Thus, the difference in temperature between the top and bottom oil should be small. To obtain this result more rapidly, the oil may be circulated by a pump. Before SCW test for LV winding resistance (Unit: ohm) | 9 observation; Value upto 1 decimal place |  | Cl.10.2 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of Winding Resistance
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 a) | Measurement of Winding Resistance | Yes | Mandatory | 10.2 Oil-Immersed Type Transformers , after the transformer has been under oil without excitation for atleast 3 h, the average oil temperature shall be determined and the temperature of the winding shall be deemed to be the same as the average oil temperature. The average oil temperature is taken as the mean of the top and bottom oil temperatures. In measuring the cold resistance for the purpose of temperature-rise determination, special efforts shall be made to determine the average winding temperature accurately. Thus, the difference in temperature between the top and bottom oil should be small. To obtain this result more rapidly, the oil may be circulated by a pump. After SCW test for LV winding resistance (Unit: ohm) | 9 observation; Value upto 1 decimal place |  | Cl.10.2 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of Winding Resistance
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 b) | Measurement of voltage ratio and check of phase displacement | Yes | Mandatory | The voltage ratio shall be measured on each tapping. The polarity of single-phase transformers and the connection symbol of three-phase transformers shall be checked. Before SCW test for Measurment of voltage ratio (Unit: volts) (Min Value : 87.6 ; Max Value : 88.4 ) | 2 observation; Value upto 1 decimal place |  | Cl.10.3 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of voltage ratio and check of phase displacement
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 b) | Measurement of voltage ratio and check of phase displacement | Yes | Mandatory | The voltage ratio shall be measured on each tapping. The polarity of single-phase transformers and the connection symbol of three-phase transformers shall be checked. After SCW test for Measurment of voltage ratio (Unit: volts) (Min Value : 87.6 ; Max Value : 88.4 ) | 2 observation; Value upto 1 decimal place |  | Cl.10.3 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of voltage ratio and check of phase displacement
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 c), 6.8. , Table 3 | Measurement of short- circuit impedance (principal tapping, when applicable) & load loss at 50 % & 100 % load | Yes | Mandatory | 50 percent of rated load and total losses values given in Table 3. (Unit: Load losses in %) (Min Value : 4.05 ; Max Value : 4.95 ) | 6 observation; Value upto 1 decimal place |  | Cl.10.4 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of short- circuit impedance (principal tapping, when applicable) & load loss at 50 % & 100 % load | [17 empty] | 135 |  | 120 |  | 108 |  | 97 |  | 87 |  | 190 |  | 175 |  | 158 |  | 142 |  | 128 |  | 340 |  | 300 |  | 270 |  | 243 |  | 219 |  | 475 |  | 435 |  | 392 |  | 352 |  | 317 |  | 670 |  | 570 |  | 513 |  | 462 |  | 416 |  | 780 |  | 670 |  | 603 |  | 543 |  | 488 |  | 141.75 |  | 126 |  | 113.4 |  | 101.85 |  | 91.35 |  | 199.5 |  | 183.75 |  | 165.9 |  | 149.1 |  | 134.4 |  | 357 |  | 315 |  | 283.5 |  | 255.15 |  | 229.95 |  | 498.75 |  | 456.75 |  | 411.6 |  | 369.6 |  | 332.85 |  | 703.5 |  | 598.5 |  | 538.65 |  | 484.05 |  | 436.8 |  | 819 |  | 703.5 |  | 633.15 |  | 569.1 |  | 511.35 |  | 145.125 |  | 129 |  | 116.1 |  | 104.275 |  | 93.525 |  | 204.25 |  | 188.125 |  | 169.85 |  | 152.65 |  | 137.6 |  | 365.5 |  | 322.5 |  | 290.25 |  | 261.225 |  | 235.425 |  | 510.625 |  | 467.625 |  | 421.4 |  | 378.4 |  | 340.775 |  | 720.25 |  | 612.75 |  | 551.475 |  | 496.65 |  | 447.2 |  | 838.5 |  | 720.25 |  | 648.225 |  | 583.725 |  | 524.6
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 c), 6.8. , Table 3 | Measurement of short- circuit impedance (principal tapping, when applicable) & load loss at 50 % & 100 % load | Yes | Mandatory | 100 percent of rated load shall not exceed the maximum total loss values given in Table 3. (Unit: Load losses in %) (Min Value : 4.05 ; Max Value : 4.95 ) | 6 observation; Value upto 1 decimal place |  | Cl.10.4 | IS 2026 (Part 1) | [21 empty] | 440 |  | 400 |  | 364 |  | 331 |  | 301 |  | 635 |  | 595 |  | 541 |  | 493 |  | 448 |  | 1140 |  | 1050 |  | 956 |  | 870 |  | 791 |  | 1650 |  | 1500 |  | 1365 |  | 1242 |  | 1130 |  | 1950 |  | 1700 |  | 1547 |  | 1408 |  | 1281 |  | 2300 |  | 2100 |  | 1911 |  | 1739 |  | 1582 |  | 462 |  | 420 |  | 382.2 |  | 348.6 |  | 316.05 |  | 666.75 |  | 624.75 |  | 567.45 |  | 517.65 |  | 470.4 |  | 1197 |  | 1102.5 |  | 1003.8 |  | 904.05 |  | 830.55 |  | 1732.5 |  | 1575 |  | 1433.25 |  | 1304.1 |  | 1179.15 |  | 2047.5 |  | 1750 |  | 1587.6 |  | 1457.4 |  | 1319.85 |  | 2415 |  | 2205 |  | 2005.5 |  | 1825.95 |  | 1661.1 |  | 473 |  | 430 |  | 391.3 |  | 355.825 |  | 323.575 |  | 682.625 |  | 639.625 |  | 581.575 |  | 529.975 |  | 481.6 |  | 1225.5 |  | 1128.75 |  | 1027.7 |  | 935.25 |  | 850.325 |  | 1773.75 |  | 1612.5 |  | 1467.375 |  | 1335.15 |  | 1214.75 |  | 2096.25 |  | 1827.5 |  | 1662.025 |  | 1513.6 |  | 1377.075 |  | 2472.5 |  | 2257.5 |  | 2054.625 |  | 1859.925 |  | 1698.15
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 c), 7.8, Table 6 | Measurement of short- circuit impedance (principal tapping, when applicable) & load loss at 50 % & 100 % load | Yes | Mandatory | 50 percent of rated load and total losses values given in Table 6 (Unit: Load losses in %) (Min Value : 4.05 ; Max Value : 4.95 ) | 6 observation; Value upto 1 decimal place |  | Cl.10.4 | IS 2026 (Part 1) | [201 empty] | 980 |  | 920 |  | 864 |  | 811 |  | 761 |  | 1025 |  | 955 |  | 890 |  | 829 |  | 772 |  | 1225 |  | 1150 |  | 1080 |  | 1013 |  | 951 |  | 1510 |  | 1430 |  | 1354 |  | 1282 |  | 1215 |  | 1860 |  | 1745 |  | 1637 |  | 1536 |  | 1441 |  | 2287 |  | 2147 |  | 2015 |  | 1892 |  | 1776 |  | 2790 |  | 2620 |  | 2460 |  | 2310 |  | 2170 |  | 3300 |  | 3220 |  | 3142 |  | 3066 |  | 2991 |  | 4200 |  | 3970 |  | 3753 |  | 3547 |  | 3353 |  | 5050 |  | 4790 |  | 4543 |  | 4309 |  | 4088 |  | 6150 |  | 5900 |  | 5660 |  | 5430 |  | 5209 |  | 1029 |  | 966 |  | 907.2 |  | 851.55 |  | 799.05 |  | 1076.25 |  | 1002.75 |  | 934.5 |  | 870.45 |  | 810.65 |  | 1286.25 |  | 1207.5 |  | 1134 |  | 1063.65 |  | 998.55 |  | 1585.5 |  | 1501.5 |  | 1421.7 |  | 1346.2 |  | 1275.75 |  | 1953 |  | 1832.25 |  | 1718.85 |  | 1612.8 |  | 1513.05 |  | 2401.35 |  | 2254.35 |  | 2115.75 |  | 1986.6 |  | 1864.8 |  | 2929.5 |  | 2751 |  | 2583 |  | 2425.5 |  | 2278.5 |  | 3465 |  | 3381 |  | 3299.1 |  | 8219.3 |  | 2090.55 |  | 4410 |  | 4068.5 |  | 3940.65 |  | 3724.35 |  | 3520.65 |  | 5302.5 |  | 5029.5 |  | 4770.15 |  | 4524.45 |  | 4292.4 |  | 6457.5 |  | 6195 |  | 2945 |  | 5701.5 |  | 5469.45 |  | 1053.5 |  | 989 |  | 928.8 |  | 871.825 |  | 818.075 |  | 1101.875 |  | 1026.625 |  | 956.75 |  | 891.175 |  | 829.9 |  | 1316.875 |  | 1236.25 |  | 1161 |  | 1088.975 |  | 1022.325 |  | 1623.25 |  | 1537.25 |  | 1455.55 |  | 1378.15 |  | 1306.125 |  | 1999.5 |  | 1875.875 |  | 1759.775 |  | 1651.2 |  | 1549.075 |  | 2458.525 |  | 2308.025 |  | 2166.125 |  | 2033.9 |  | 1909.2 |  | 2999.25 |  | 2816.5 |  | 2644.5 |  | 2483.25 |  | 2332.75 |  | 3547.5 |  | 3461.5 |  | 3377.65 |  | 3295.95 |  | 3215.325 |  | 4515 |  | 4267.75 |  | 4034.475 |  | 3813.525 |  | 3604.475 |  | 5428.75 |  | 5149.25 |  | 4883.725 |  | 4632.175 |  | 4394.6 |  | 6611.25 |  | 6342.5 |  | 6084.5 |  | 5837.25 |  | 5599.675 |  | 35 |  | 30 |  | 27 |  | 24 |  | 21 |  | 60 |  | 55 |  | 50 |  | 45 |  | 40 |  | 82 |  | 63 |  | 58 |  | 54 |  | 50 |  | 110 |  | 95 |  | 88 |  | 80 |  | 74 |  | 210 |  | 190 |  | 177 |  | 160 |  | 148 |  | 310 |  | 285 |  | 265 |  | 242 |  | 223 |  | 410 |  | 375 |  | 350 |  | 320 |  | 299 |  | 36.75 |  | 31.5 |  | 28.35 |  | 25.2 |  | 22.05 |  | 63 |  | 57.75 |  | 52.5 |  | 47.25 |  | 42 |  | 86.1 |  | 66.15 |  | 60.9 |  | 56.7 |  | 52.5 |  | 115.5 |  | 99.75 |  | 92.4 |  | 84 |  | 77.7 |  | 220.5 |  | 199.5 |  | 185.85 |  | 168 |  | 155.4 |  | 325.5 |  | 299.25 |  | 278.25 |  | 254.1 |  | 234.15 |  | 430.5 |  | 393.75 |  | 367.5 |  | 336 |  | 313.95 |  | 37.625 |  | 32.25 |  | 29.025 |  | 25.8 |  | 22.575 |  | 64.5 |  | 59.125 |  | 53.75 |  | 48.375 |  | 43 |  | 88.15 |  | 67.725 |  | 62.35 |  | 58.05 |  | 53.75 |  | 118.25 |  | 102.125 |  | 94.6 |  | 86 |  | 79.55 |  | 225.75 |  | 204.25 |  | 190.275 |  | 172 |  | 159.1 |  | 333.25 |  | 306.375 |  | 284.875 |  | 260.15 |  | 239.725 |  | 440.75 |  | 403.125 |  | 376.25 |  | 344 |  | 321.425
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 c), 7.8, Table 6 | Measurement of short- circuit impedance (principal tapping, when applicable) & load loss at 50 % & 100 % load | Yes | Mandatory | 100 percent of rated load shall not exceed the maximum total loss values given in Table 6 (Unit: Load losses in %) (Min Value : 4.05 ; Max Value : 4.95 ) | 6 observation; Value upto 1 decimal place |  | Cl.10.4 | IS 2026 (Part 1) | [201 empty] | 2930 |  | 2700 |  | 2488 |  | 2293 |  | 2113 |  | 3100 |  | 2750 |  | 2440 |  | 2164 |  | 1920 |  | 3450 |  | 3330 |  | 3214 |  | 3102 |  | 2994 |  | 4300 |  | 4100 |  | 3909 |  | 3727 |  | 3554 |  | 5300 |  | 4850 |  | 4438 |  | 4061 |  | 3717 |  | 6403 |  | 5838 |  | 5323 |  | 4853 |  | 4425 |  | 7700 |  | 7000 |  | 6364 |  | 5785 |  | 5259 |  | 9200 |  | 8400 |  | 7670 |  | 7003 |  | 6394 |  | 11800 |  | 11300 |  | 10821 |  | 10363 |  | 9924 |  | 15000 |  | 14100 |  | 13254 |  | 12459 |  | 11711 |  | 18500 |  | 17500 |  | 16554 |  | 15659 |  | 14813 |  | 3076.5 |  | 2835 |  | 2612.4 |  | 2407.65 |  | 2218.65 |  | 3255 |  | 2887.5 |  | 2562 |  | 2272.2 |  | 2016 |  | 3622.5 |  | 3496.5 |  | 3374.7 |  | 3257.1 |  | 3143.7 |  | 4515 |  | 4305 |  | 4104.45 |  | 3913.35 |  | 3731.7 |  | 5565 |  | 5092.5 |  | 4659.9 |  | 4264.05 |  | 3902.85 |  | 6723.2 |  | 6057.9 |  | 5589.15 |  | 5095.65 |  | 4646.25 |  | 8085 |  | 7350 |  | 6682.2 |  | 6074.25 |  | 5521.95 |  | 9660 |  | 8820 |  | 8053.5 |  | 7353.15 |  | 6713.7 |  | 12390 |  | 11865 |  | 11362.05 |  | 10881.15 |  | 10420.2 |  | 15750 |  | 14805 |  | 13916.7 |  | 13081.95 |  | 12296.55 |  | 19425 |  | 18375 |  | 17381.7 |  | 16441.95 |  | 15553.65 |  | 3149.75 |  | 2902.5 |  | 2674.6 |  | 2464.975 |  | 2271.475 |  | 3332.5 |  | 2956.25 |  | 2623 |  | 2326.3 |  | 2064 |  | 3708.75 |  | 3579.75 |  | 3455.05 |  | 3334.65 |  | 3218.55 |  | 4622.5 |  | 4407.5 |  | 4202.175 |  | 4006.525 |  | 3820.55 |  | 5697.5 |  | 5213.75 |  | 4770.85 |  | 4365.575 |  | 3995.775 |  | 6883.225 |  | 6275.85 |  | 5722.225 |  | 5216.975 |  | 4756.875 |  | 8277.5 |  | 7525 |  | 6841.3 |  | 6218.875 |  | 5653.425 |  | 9890 |  | 9030 |  | 8245.25 |  | 7528.225 |  | 6873.55 |  | 12685 |  | 12147.5 |  | 11632.575 |  | 11140.225 |  | 10668.3 |  | 16125 |  | 15157.5 |  | 14248.05 |  | 13393.425 |  | 12589.325 |  | 19887.5 |  | 18812.5 |  | 17795.55 |  | 16833.425 |  | 15923.975 |  | 95 |  | 75 |  | 68 |  | 62 |  | 57 |  | 170 |  | 150 |  | 135 |  | 122 |  | 112 |  | 224 |  | 190 |  | 175 |  | 164 |  | 145 |  | 300 |  | 260 |  | 240 |  | 225 |  | 210 |  | 590 |  | 520 |  | 480 |  | 451 |  | 420 |  | 880 |  | 780 |  | 720 |  | 670 |  | 625 |  | 1140 |  | 1030 |  | 964 |  | 900 |  | 842 |  | 99.75 |  | 78.75 |  | 71.4 |  | 65.1 |  | 59.85 |  | 178.5 |  | 157.5 |  | 141.75 |  | 128.1 |  | 117.6 |  | 235.2 |  | 199.5 |  | 183.75 |  | 172.2 |  | 152.25 |  | 315 |  | 273 |  | 252 |  | 236.25 |  | 220.5 |  | 619.5 |  | 546 |  | 504 |  | 473.55 |  | 441 |  | 924 |  | 819 |  | 756 |  | 703.5 |  | 656.25 |  | 1197 |  | 1081.5 |  | 1012.2 |  | 945 |  | 884.1 |  | 102.125 |  | 80.625 |  | 73.1 |  | 66.65 |  | 61.275 |  | 182.75 |  | 161.25 |  | 145.125 |  | 131.15 |  | 120.4 |  | 240.8 |  | 204.25 |  | 188.125 |  | 176.3 |  | 155.875 |  | 322.5 |  | 279.5 |  | 258 |  | 241.875 |  | 225.75 |  | 634.25 |  | 559 |  | 516 |  | 484.825 |  | 451.5 |  | 946 |  | 838.5 |  | 774 |  | 720.25 |  | 671.875 |  | 1225.5 |  | 1107.25 |  | 1036.3 |  | 967.5 |  | 905.15
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 c), 8.8, Table 9 | Measurement of short- circuit impedance (principal tapping, when applicable) & load loss at 50 % & 100 % load | Yes | Mandatory | 50 percent of rated load and total losses values given in Table 9 (Unit: Load losses in %) (Min Value : 4.05 ; Max Value : 4.95 ) | 6 observation; Value upto 1 decimal place |  | Cl.10.4 | IS 2026 (Part 1)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 c), 8.8, Table 9 | Measurement of short- circuit impedance (principal tapping, when applicable) & load loss at 50 % & 100 % load | Yes | Mandatory | 100 percent of rated load shall not exceed the maximum total loss values given in Table 9 (Unit: Load losses in %) (Min Value : 4.05 ; Max Value : 4.95 ) | 6 observation; Value upto 1 decimal place |  | Cl.10.4 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of short- circuit impedance (principal tapping, when applicable) & load loss at 50 % & 100 % load
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 d) | Measurement of no-load loss & Current | Yes | Mandatory | The no-load loss and the no-load current shall be measured on one of the windings at rated frequency and at a voltage corresponding to rated voltage if the test is performed on the principal tapping, or to the appropriate tapping voltage if the test is performed on another tapping. The remaining winding or windings shall be left open-circuited and any windings which can be connected in open delta shall have the delta closed. Before SCW test for Measurement of no-load loss (Unit: Load losses in %) ( Max Value : 1.0) | 4 observation; Value upto 1 decimal place |  | Cl.10.5 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of no-load loss & Current
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 d) | Measurement of no-load loss & Current | Yes | Mandatory | The no-load loss and the no-load current shall be measured on one of the windings at rated frequency and at a voltage corresponding to rated voltage if the test is performed on the principal tapping, or to the appropriate tapping voltage if the test is performed on another tapping. The remaining winding or windings shall be left open-circuited and any windings which can be connected in open delta shall have the delta closed. After SCW test for Measurement of no-load loss (Unit: Load losses in %) ( Max Value : 1.0) | 4 observation; Value upto 1 decimal place |  | Cl.10.5 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of no-load loss & Current
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 d) | Measurement of no-load loss & Current | Yes | Mandatory | The no-load loss and the no-load current shall be measured on one of the windings at rated frequency and at a voltage corresponding to rated voltage if the test is performed on the principal tapping, or to the appropriate tapping voltage if the test is performed on another tapping. The remaining winding or windings shall be left open-circuited and any windings which can be connected in open delta shall have the delta closed. Before SCW test for Measurement of no-load current (Unit: Amps) ( Max Value : 1.0) | 4 observation; Value upto 1 decimal place |  | Cl.10.5 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of no-load loss & Current
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 d) | Measurement of no-load loss & Current | Yes | Mandatory | The no-load loss and the no-load current shall be measured on one of the windings at rated frequency and at a voltage corresponding to rated voltage if the test is performed on the principal tapping, or to the appropriate tapping voltage if the test is performed on another tapping. The remaining winding or windings shall be left open-circuited and any windings which can be connected in open delta shall have the delta closed. After SCW test for Measurement of no-load current (Unit: Amps) ( Max Value : 1.0) | 4 observation; Value upto 1 decimal place |  | Cl.10.5 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of no-load loss & Current
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.2 e) | Measurement of insulation resistance | Yes | Mandatory | The capacitance measured does not deviate from the true value by more than 0,2 % (Unit: ohm) | 1 observation; Value upto 1 decimal place |  | Cl.11.5 | IS 2026 (Part 1) |  |  |  | Single Observation for Measurement of insulation resistance
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.2 f) | Induced over-voltage withstand test | Yes | Mandatory | The test voltage of 866 Volts, 3 – phase was applied to the LV winding of the transformer and HV winding kept open. The supply frequency was maintained at 150 Hz. The test voltage was applied for 40 seconds. | Satisfactory/Unsatisfactory |  |  | IS 2026 (Part 3) |  |  |  | 1 observation; Value upto 1 decimal place
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.2 g) | Separate-source voltage withstand test | Yes | Mandatory | HV winding: The test voltage of 28 kV ac, rms was applied between the shorted HV winding and earth. The tank and LV winding were shorted together and earthed. The test voltage was applied for 60 seconds. | Satisfactory/Unsatisfactory |  |  | IS 2026 (Part 3) |  |  |  | 2 observation; Value upto 1 decimal place
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.2 g) | Separate-source voltage withstand test | Yes | Mandatory | LV winding: The test voltage of 3 kV ac, rms was applied between the shorted LV winding and earth. The tank and HV winding were shorted together and earthed. The test voltage was applied for 60 seconds. | Satisfactory/Unsatisfactory |  |  | IS 2026 (Part 3) |  |  |  | 2 observation; Value upto 1 decimal place
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.2 h), 15.2 | Pressure Test | Yes | Mandatory | For non-sealed and sealed type transformers, the transformer tank shall be subjected to air pressure of 80 kPa for 30 min and vacuum of 250 mm of mercury for 30 min | Satisfactory/Unsatisfactory | kPa, mm | Cl.21.5.1.1 | IS 1180 (Part 1) |  |  |  | 1 observation; Value upto 1 decimal place
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.2 j), 15.2 | Oil leakage test | Yes | Mandatory | The assembled transformer for non-sealed and sealed type with all fittings including bushings in position, shall be tested at a pressure equivalent to twice the normal head measured at the base of the tank for 8 h. | Satisfactory/Unsatisfactory | kPa, mm | Cl.21.5.1.3 | IS 1180 (Part 1)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.2 j), 15.2 | Oil leakage test | Yes | Mandatory | There should be no leakage at any point. Tank with corrugations shall be tested for oil leakage test a pressure of 15 kPa measured at the top of the tank for 6 h. There should be no leakage at any point. | Satisfactory/Unsatisfactory | kPa, mm | Cl.21.5.1.3 | IS 1180 (Part 1)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.3 (a) | Lightning impulse test | Yes | Mandatory | The test impulse shall be a full standard lightning impulse: 1,2 ± 30 % / 50 µs ± 20 %.. The test voltage value shall be the test voltage value as defined in IEC 60060-1 (after the test voltage function is applied). | Satisfactory/Unsatisfactory | In accordance with Cl. No 13.2, 13.3 13.4 in IS: 2026 Part 3 | Cl.13.2, 13.3 & 13.4 | IS 2026 (Part 3)
[5 empty] | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.3 (a) | Lightning impulse test | Yes | Mandatory | If the maximum relative overshoot magnitude is 5 % or less, the test voltage value may be taken as the extreme value as defined in IEC 60060-1. The tolerance on the test voltage value is ± 3 % | Satisfactory/Unsatisfactory | In accordance with Cl. No 13.2, 13.3 13.4 in IS: 2026 Part 3 | Cl.13.2, 13.3 & 13.4 | IS 2026 (Part 3)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.3 (b), 6.10, 7.10,8.10 | Temperature-rise test | Yes | Mandatory | Maximum measured total loss (No load at rated excitation + load loss at maximum current tap converted to 75 ºC reference temperature) at 100 percent loading shall be supplied during temperature rise test. (Unit: °C) (Max Value : 40.0) | Satisfactory/Unsatisfactory | In accordance with Cl. No 5 of IS: 2026 Part 2 | Cl.5 | IS 2026 (Part 2) |  |  |  | Single Observation forTemperature-rise test
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.3 (C ),17 | Short-circuit withstand test | Yes | Mandatory | The requirements of this clause apply to both oilimmersed and dry-type transformers as specified in IS 2026 (Part 1) and IS 2026 (Part 2), respectivelyThe requirements of this clause apply to both oilimmersed and dry-type transformers as specified in IS 2026 (Part 1) and IS 2026 (Part 2), respectively (Max Value: 2.0) | Satisfactory/Unsatisfactory | In accordance with Cl. No 4 of IS: 2026 Part 5 | Cl.4 | IS 2026 (Part 5) |  |  |  | Single Observation for Short-circuit withstand test
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Quantitative | 21.5.1.1 | Pressure test (type test) | Yes | Mandatory | For non-sealed and sealed type transformers, the transformer tank shall be subjected to air pressure of 80 kPa for 30 min and vacuum of 250 mm of mercury for 30 min.(Max Value: 6.5 mm) | Satisfactory/Unsatisfactory | kPa | Cl.21.5.1.1 | IS 1180 (Part 1) |  |  |  | Single Observation for Pressure test (type test)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.5.1.2 | Pressure (routine test) | Yes | Mandatory | a) Non-sealed type transformers (plain tanks) The transformer with bolted cover shall be tested at an air pressure of 35 kPa above atmosphere pressure maintained inside the tank for 10 min. There should be no leakage at any point. | Satisfactory/Unsatisfactory | kPa |  | IS 1180 (Part 1)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.5.1.2 | Pressure (routine test) | Yes | Mandatory | b) Corrugated tanks The corrugated transformer tank shall be tested for air pressure of 15 kPa above atmosphere pressure maintained inside the tank for 10 min. There should be no leakage at any point. | Satisfactory/Unsatisfactory | kPa |  | IS 1180 (Part 1)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.5.1.2 | Pressure (routine test) | Yes | Mandatory | c) Sealed type transformers The transformer with welded cover shall be tested at an air pressure of 80 kPa above atmosphere pressure maintained inside the tank for 10 min. There should be no leakage at any point. | Satisfactory/Unsatisfactory | kPa |  | IS 1180 (Part 1)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.5.1.3 | Oil leakage (routine test) | Yes | Mandatory | The condition, workmanship, marking and finish shall be satisfactory. The marking shall be legible during the life of the capacitor. There shall be no seepage of any filling material or other visible damage. | Satisfactory/Unsatisfactory |  |  | IS 1180 (Part 1)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.4 a | Determination of sound levels | Yes | Mandatory | The test shall be carriedout as per Cl.21.4(a) of IS 2026: Part 10. The sound level measured in the test according to IEC 60076-10 shall not exceed the guaranteed maximum sound level. The guaranteed maximum sound level is a limit without tolerance. | Satisfactory/Unsatisfactory |  |  | IS 2026 (Part 10)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.4 b | Short-circuit withstand test | Yes | Mandatory | The requirements of this clause apply to both oil immersed and dry-type transformers as specified in IS 2026 (Part 1) and IS 2026 (Part 2), respectively. | Satisfactory/Unsatisfactory |  | Cl.4 | IS 2026 (Part 5)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.4 c | No load current at 112.5 % voltage | Yes | Mandatory | No-load current up to 200 kVA shall not exceed 3 percent of full load current and will be measured by energizing the transformer at rated voltage and frequency. Increase of 12.5 percent of rated voltage shall not increase the no load current by 6 percent maximum of full load current. (Max Value: 2.0) | Satisfactory/Unsatisfactory |  |  | IS 1180 (Part 1) |  |  |  | Single Observation for No load current
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.4 d | Paint adhesion tests | Yes | Mandatory | Paint adhesion tests. The test is performed as per ASTM D3359 | Satisfactory/Unsatisfactory |  |  | IS 1180 (Part 1)
IS 1180 | 1 | N.A. | 2014 | 4 | Outdoor/Indoor Type Oil Immersed Distribution Transformers Upto and Including 2 500 kVA, 33kV — Specification: Part 1 Mineral Oil Immersed | Electrical | Qualitative | 21.4 e | BDV and moisture content of oil in the transformer | Yes | Mandatory | Breakdown voltage shall be measured in accordance with IS 6792. The oil shall have a high dielectric strength (breakdown voltage >70 kV). | Satisfactory/Unsatisfactory |  |  | IS 335 |  |  |  | Single Observation for No load current