## 13095 TRep
IS Number | Part | Section | Year | Number of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause/ Table/ Annex Reference | Test Parameter Name | To be tested and/or reported by Lab (Yes/No) | Mandatory or Optional | Requirement (as per Indian Standard) - No specified values to be mentioned here | Test Result/ Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference | Sample Quantity | Equipment | Remarks | Specified limits for PN 2.5 - Class 125/50 - DN 40 | Specified limits for PN 2.5 - Class 125/50 - DN 40 | Specified limits for PN 2.5 - Class 125/50 - DN 50 | Specified limits for PN 2.5 - Class 125/50 - DN 50 | Specified limits for PN 2.5 - Class 125/50 - DN 65 | Specified limits for PN 2.5 - Class 125/50 - DN 65 | Specified limits for PN 2.5 - Class 125/50 - DN 80 | Specified limits for PN 2.5 - Class 125/50 - DN 80 | Specified limits for PN 2.5 - Class 125/50 - DN 100 | Specified limits for PN 2.5 - Class 125/50 - DN 100 | Specified limits for PN 2.5 - Class 125/50 - DN 125 | Specified limits for PN 2.5 - Class 125/50 - DN 125 | Specified limits for PN 2.5 - Class 125/50 - DN 150 | Specified limits for PN 2.5 - Class 125/50 - DN 150 | Specified limits for PN 2.5 - Class 125/50 - DN 200 | Specified limits for PN 2.5 - Class 125/50 - DN 200 | Specified limits for PN 2.5 - Class 125/50 - DN 250 | Specified limits for PN 2.5 - Class 125/50 - DN 250 | Specified limits for PN 2.5 - Class 125/50 - DN 300 | Specified limits for PN 2.5 - Class 125/50 - DN 300 | Specified limits for PN 2.5 - Class 125/50 - DN 350 | Specified limits for PN 2.5 - Class 125/50 - DN 350 | Specified limits for PN 2.5 - Class 125/50 - DN 400 | Specified limits for PN 2.5 - Class 125/50 - DN 400 | Specified limits for PN 2.5 - Class 125/50 - DN 450 | Specified limits for PN 2.5 - Class 125/50 - DN 450 | Specified limits for PN 2.5 - Class 125/50 - DN 500 | Specified limits for PN 2.5 - Class 125/50 - DN 500 | Specified limits for PN 2.5 - Class 125/50 - DN 600 | Specified limits for PN 2.5 - Class 125/50 - DN 600 | Specified limits for PN 2.5 - Class 125/50 - DN 700 | Specified limits for PN 2.5 - Class 125/50 - DN 700 | Specified limits for PN 2.5 - Class 125/50 - DN 800 | Specified limits for PN 2.5 - Class 125/50 - DN 800 | Specified limits for PN 2.5 - Class 125/50 - DN 900 | Specified limits for PN 2.5 - Class 125/50 - DN 900 | Specified limits for PN 2.5 - Class 125/50 - DN 1000 | Specified limits for PN 2.5 - Class 125/50 - DN 1000 | Specified limits for PN 2.5 - Class 125/50 - DN 1200 | Specified limits for PN 2.5 - Class 125/50 - DN 1200 | Specified limits for PN 2.5 - Class 125/50 - DN 1400 | Specified limits for PN 2.5 - Class 125/50 - DN 1400 | Specified limits for PN 2.5 - Class 125/50 - DN 1600 | Specified limits for PN 2.5 - Class 125/50 - DN 1600 | Specified limits for PN 2.5 - Class 125/50 - DN 1800 | Specified limits for PN 2.5 - Class 125/50 - DN 1800 | Specified limits for PN 2.5 - Class 125/50 - DN 2000 | Specified limits for PN 2.5 - Class 125/50 - DN 2000 | Specified limits for PN 4.0 - Class 300 - DN 40 | Specified limits for PN 4.0 - Class 300 - DN 40 | Specified limits for PN 4.0 - Class 300 - DN 50 | Specified limits for PN 4.0 - Class 300 - DN 50 | Specified limits for PN 4.0 - Class 300 - DN 65 | Specified limits for PN 4.0 - Class 300 - DN 65 | Specified limits for PN 4.0 - Class 300- DN 80 | Specified limits for PN 4.0 - Class 300 - DN 80 | Specified limits for PN 4.0 - Class 300- DN 100 | Specified limits for PN 4.0 - Class 300 - DN 100 | Specified limits for PN 4.0 - Class 300 - DN 125 | Specified limits for PN 4.0 - Class 300 - DN 125 | Specified limits for PN 4.0 - Class 300 - DN 150 | Specified limits for PN 4.0 - Class 300 - DN 150 | Specified limits for PN 4.0 - Class 300- DN 200 | Specified limits for PN 4.0 - Class 300 - DN 200 | Specified limits for PN 4.0 - Class 300- DN 250 | Specified limits for PN 4.0 - Class 300 - DN 250 | Specified limits for PN 4.0 - Class 300 - DN 300 | Specified limits for PN 4.0 - Class 300 - DN 300 | Specified limits for PN 4.0 - Class 300- DN 350 | Specified limits for PN 4.0 - Class 300 - DN 350 | Specified limits for PN 4.0 - Class 300 - DN 400 | Specified limits for PN 4.0 - Class 300- DN 400 | Specified limits for PN 4.0 - Class 300 - DN 450 | Specified limits for PN 4.0 - Class 300 - DN 450 | Specified limits for PN 4.0 - Class 300 - DN 500 | Specified limits for PN 4.0 - Class 300 - DN 500 | Specified limits for PN 4.0 - Class 300 - DN 600 | Specified limits for PN 4.0 - Class 300 - DN 600 | Specified limits for PN 4.0 - Class 300 - DN 700 | Specified limits for PN 4.0 - Class 300 - DN 700 | Specified limits for PN 4.0 - Class 300 - DN 800 | Specified limits for PN 4.0 - Class 300- DN 800 | Specified limits for PN 4.0 - Class 300 - DN 900 | Specified limits for PN 4.0 - Class 300 - DN 900 | Specified limits for PN 4.0 - Class 300 - DN 1000 | Specified limits for PN 4.0 - Class 300 - DN 1000 | Specified limits for PN 4.0 - Class 300 - DN 1200 | Specified limits for PN 4.0 - Class 300 DN 1200 | Specified limits for PN 4.0 - Class 300 - DN 1400 | Specified limits for PN 4.0 - Class 300- DN 1400 | Specified limits for PN 4.0 - Class 300 - DN 1600 | Specified limits for PN 4.0 - Class 300- DN 1600 | Specified limits for PN 4.0 - Class 300 - DN 1800 | Specified limits for PN 4.0 - Class 300 - DN 1800 | Specified limits for PN 4.0 - Class 300- DN 2000 | Specified limits for PN 4.0 - Class 300 - DN 2000 | Specified limits for Tight shut-off | Specified limits for Tight shut-off | Specified limits for Low leakage | Specified limits for Low leakage | Specified limits for Regulating | Specified limits for Regulating | If the test is quantitative, the Min and Max value to be written after applying the tolerance given in the standard. If only upper and lower limit is given, mention ONLY Min or ONLY Max balue and leave the other cell blank. If the test is Qualitative, both Only Min column to be filled by the qualitiative requirement, the Max column to be left blank
THIS ROW TO BE LEFT BLANK | [20 empty] | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 4 | Valve end connections | Yes | Mandatory | Valve end connections | To be checked on declaration bais | Declaration of Valve End Connections as per Fig. 1 / 2 / 3 / 4 / 5 / 6 | 4 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 5 | Service Applications | Yes | Mandatory | Service Applications | To be checked on declaration bais | Declaration of Valve Applications | 5 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Quantitative | 6 | NOMINAL SIZES | Yes | Mandatory | Nominal valve size (DN), mm | Value upto 0 decimal places | Declaration of Nominal valve size (DN) | 6 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Quantitative | 7.1 | NOMINAL PRESSURES | Yes | Mandatory | Nominal pressure (PN), MPa | Value upto 2 decimal places | Declaration of Nominal pressure (PN) | 7.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 7.2 | NOMINAL PRESSURES | Yes | Mandatory | Material | To be checked on declaration bais | Declaration of Material | 7.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 7.2 | NOMINAL PRESSURES | Yes | Mandatory | Nominal Pipe Size | To be checked on declaration bais | Declaration of Nominal Pipe Size | 7.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 7.2 | NOMINAL PRESSURES | Yes | Mandatory | Class | To be checked on declaration bais | Declaration of Class | 7.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 8 | Pressure/Temperature Ratings | Yes | Mandatory | Maximum permissible gauge working pressure and operating temperature shall be in accordance with IS 6418 and IS 13159 (Part 1) except that restrictions on temperature may be placed by the manufacturer on valves in accordance with this standard by reason of valve type, trim material or other factors. | To be checked on declaration bais | Declaration of Compliance to Pressure/Temperature Ratings | 8 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 8 | Pressure/Temperature Ratings | Yes | Mandatory | All valves shall be suitable for continuous use at their PN designation within the temperature range of -100C to 65°C. | To be checked on declaration bais | Declaration of Compliance to Pressure/Temperature Ratings | 8 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 9.1 | Double Flanged Body Ends | Yes | Mandatory | The dimensions of flanged body ends and drillings shall be in accordance with the requirement given in Annex B. | Please see the Test Report of IS 6418, IS 6392, IS 9523 | Declaration of Material Declaration of Nominal Pressure Declaration if material to be tested as per IS 6418, IS 6392, and IS 9523 | 9.1 | 13095 |  |  |  | Separate format required for IS 6418, IS 6392, and IS 9523 and test request shall be initiated if testing as per this clause is required.
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 9.1 | Double Flanged Body Ends | Yes | Optional | Flanges as per any other specific requirements of the purchaser may also be given as agreed to between the manufacturer and the purchaser or as per IS 13159 (Part 1). | Please see the Test Report of IS 13159 (Part 1) | Declaration of specified requirements Declaration if material to be tested as per IS 13159 (Part 1) | 9.1 | 13159 (Part 1). |  |  |  | Separate format required for IS 13159 and test request shall be initiated if testing as per this clause is required.
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 9.1.1 | Body Ends | Yes | Mandatory | Flanges shall be at right angles to the axis of the bore and concentric with the bore. | Satisfactory/Unsatisfactory with details |  | 9.1.1 | 13095 | 1
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 9.1.1 | Body Ends | Yes | Mandatory | Flanges shall be drilled unless otherwise specified and bolt holes shall be off centres. | Satisfactory/Unsatisfactory with details | Declaration if Flanges are drilled | 9.1.1 | 13095 | 2
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 9.1.1 | Body Ends | Yes | Mandatory | Tapped holes in the flanges may be used when required by the design of the valve | Satisfactory/Unsatisfactory with details |  | 9.1.1 | 13095 | 3
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 9.2.1 | Wafer Body Ends | Yes | Mandatory | Body ends shall be capable of being fitted between the pipe flanges complying with the requirements of Annex B flange drilling. | Satisfactory/Unsatisfactory with details |  | 9.2.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 9.2.2 | Wafer Body Ends | Yes | Mandatory | The joint faces shall be at right angles to the axis of the bore and concentric with the bore. | Satisfactory/Unsatisfactory with details |  | 9.2.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 9.2.3 | Wafer Body Ends | Yes | Mandatory | The joint faces shall be Holes may be provided, where required by the design, for the passage of the bolts securing the flanges and the valve. Where through bolting is not practicable due to the presence of valve shaft bearing housing, tapped holes may be provided for individual bolting of each flange.t right angles to the axis of the bore and concentric with the bore. | Satisfactory/Unsatisfactory with details |  | 9.2.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Quantitative | 10.1 | FACE TO FACE DIMENSIONS | Yes | Mandatory | Double Flange Short, mm | Value upto 0 decimal places | Declaration of Pressure rating Declaration of Nominal Size Declaration of Type of valve | 10.1 | 13095 | 1 |  |  |  | 104 | 108 | 106 | 110 | 110 | 114 | 112 | 116 | 125 | 129 | 138 | 142 | 138 | 142 | 150 | 154 | 163 | 167 | 176 | 180 | 188 | 192 | 214 | 218 | 220 | 224 | 227 | 231 | 264 | 270 | 289 | 295 | 315 | 321 | 327 | 333 | 407 | 413 | 467 | 473 | 526 | 534 | 596 | 604 | 666 | 674 | 756 | 764 | 104/138 | 108/142 | 106/148 | 110/152 | 110/168 | 114/172 | 112/178 | 116/182 | 125/188 | 129/192 | 138/198 | 142/202 | 138/208 | 142/212 | 150/228 | 154/232 | 163/247 | 167/253 | 176/267 | 180/273 | 188/287 | 192/293 | 214/307 | 218/313 | 220/327 | 224/333 | 227/347 | 231/353 | 264/387 | 270/393 | 289/427 | 295/433 | 315/467 | 321/473 | 327/506 | 333/514 | 407/546 | 413/554 | 467/626 | 473/634 | 526/706 | 534/714 | 596/786 | 604/794 | 664/865 | 674/875 | 756/945 | 764/955
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Quantitative | 10.1 | FACE TO FACE DIMENSIONS | Yes | Mandatory | Double Flange Long, mm | Value upto 0 decimal places | Declaration of Pressure rating Declaration of Nominal Size Declaration of Type of valve | 10.1 | 13095 | 2 |  |  |  | 163 | 167 | 176 | 180 | 188 | 192 | 201 | 205 | 227 | 231 | 251 | 257 | 263 | 270 | 289 | 295 | 327 | 333 | 353 | 359 | 378 | 384 | 403 | 409 | 429 | 435 | 454 | 460 | 504 | 512 | 606 | 614 | 656 | 664 | 707 | 715 | 808 | 818 | - | - | - | - | - | - | - | - | - | - | 188 | 192 | 214 | 218 | 239 | 243 | 280 | 286 | 302 | 308 | 378 | 384 | 400 | 406 | 416 | 422 | 454 | 460 | 498 | 506 | 758 | 766 | 833 | 843 | 909 | 919 | 986 | 996 | 1137 | 1149 | 1340 | 1352 | 1518 | 1530 | 1721 | 1733 | - | - | - | - | - | - | - | - | - | - | - | -
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Quantitative | 10.1 | FACE TO FACE DIMENSIONS | Yes | Mandatory | Wafer Short, mm | Value upto 0 decimal places | Declaration of Pressure rating Declaration of Nominal Size Declaration of Type of valve | 10.1 | 13095 | 3 |  |  |  | 31 | 35 | 41 | 45 | 44 | 48 | 44/46 | 48/50 | 50/52 | 52/56 | 54 | 58 | 54/55 | 55/59 | 58/62 | 62/66 | 66/69 | 70/73 | 76/79 | 80/83 | 76 | 80 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Quantitative | 10.1 | FACE TO FACE DIMENSIONS | Yes | Mandatory | Wafer Medium, mm | Value upto 0 decimal places | Declaration of Pressure rating Declaration of Nominal Size Declaration of Type of valve | 10.1 | 13095 | 4 |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | 94 | 100 | 104 | 112 | 116 | 125 | 129 | 152 | 156 | 163 | 167 | 188 | 192 | 198/201 | 202/205 | 248/214 | 254/218 | 273/251 | 279/257 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Quantitative | 10.1 | FACE TO FACE DIMENSIONS | Yes | Mandatory | Wafer Long, mm | Value upto 0 decimal places | Declaration of Pressure rating Declaration of Nominal Size Declaration of Type of valve | 10.1 | 13095 | 5 |  |  |  | - | - | - | - | - | - | 62 | 66 | 62 | 66 | 68 | 72 | 74 | 78 | 87 | 91 | 112 | 116 | 112 | 116 | 125 | 129 | 138 | 142 | 150 | 154 | 150 | 154 | 176 | 180 | 227 | 231 | 239 | 243 | 239 | 243 | 297 | 303 | 347 | 353 | 387 | 393 | 437 | 443 | 487 | 493 | 536 | 544 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Quantitative | 10.1 | FACE TO FACE DIMENSIONS | Yes | Mandatory | Wafer, mm | Value upto 0 decimal places | Declaration of Pressure rating Declaration of Nominal Size Declaration of Type of valve | 10.1 | 13095 | 6 | [51 empty] | - | - | - | - | - | - | 47/46 | 51/50 | 54/52 | 58/56 | 62 | 66 | 68/57 | 72/61 | 69/71 | 73/75 | 74/81 | 78/85 | 81/90 | 85/94 | 125/115 | 129/119 | 138/131 | 142/135 | 158/147 | 162/151 | 168/157 | 172/161 | 198/179 | 202/183 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 10.3 | FACE TO FACE DIMENSIONS | Yes | Mandatory | The manufacturer shall ensure that adequate space will be available between valve flanges for bolting when flanged valve with short body face to face or wafer long face to face are manufactured | Satisfactory/Unsatisfactory with details | Declaration of Pressure rating Declaration of Nominal Size Declaration of Type of valve | 10.3 | 13095 | 6 | [51 empty] | - | - | - | - | - | - | 47/46 | 51/50 | 54/52 | 58/56 | 62 | 66 | 68/57 | 72/61 | 69/71 | 73/75 | 74/81 | 78/85 | 81/90 | 85/94 | 125/115 | 129/119 | 138/131 | 142/135 | 158/147 | 162/151 | 168/157 | 172/161 | 198/179 | 202/183 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 11 | BODIES | Yes | Mandatory | Body end ports shall be circular and the numerical values of the diameter shall be as close as possible to the value of DN. | Satisfactory/Unsatisfactory with details |  | 11 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 12 | DISC AND SHAFT | Yes | Mandatory | The disc and shaft shall be designed to withstand the maximum pressure differential across the valve in either direction of flow. The shaft may be of one piece design or in two pieces separately attached to the disc. Any means of attachment between the shaft and the disc shall be, such as to preclude components becoming loose in service. Shaft design shall be anti-blowout proof design such that after removal of actuator, shaft shall remain in place withstanding the internal design pressure. For better leak tightness, double or triple eccentric valve may be provided | Satisfactory/Unsatisfactory with details |  | 12 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 13 | SEATING AND LININGS | Yes | Mandatory | Non-integral seatings, and lining where used, and their means of attachment shall be, such as to preclude their becoming loose in service. | Satisfactory/Unsatisfactory with details |  | 13 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 14.1 | BEARINGS | Yes | Mandatory | The bearings shall be suitable for the maximum loads imposed by the shaft during testing and in service. | Satisfactory/Unsatisfactory with details |  | 14.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 14.2 | BEARINGS | Yes | Mandatory | For valves DN 350 and above, a bearing shall be provided to take the axial thrust, spring retaining clips (circlips) shall not be used as thrust bearing. | Satisfactory/Unsatisfactory with details |  | 14.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 14.3 | BEARINGS | Yes | Mandatory | Suitable sealing shall be provided for the shaft where it passes outside the pressure containing enclosure. | Satisfactory/Unsatisfactory with details |  | 14.3 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 15 | MATERIALS | Yes | Mandatory | This standard is based on materials specified in Table 2. Unless otherwise agreed, the materials shall be of a grade equivalent to those given in Table 2 or superior. Other material may be used as per agreement between the manufacturer and the purchaser | To be checked on declaration bais | Declaration of material grade for Body, Disc, Shaft, Seating Ring/ Seal Retaining Ring, Seat, Shaft Bearing Seals, Internal Fastenings, External Bolting | 15 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.1 | Manual Operation | Yes | Mandatory | All valves shall be capable of being operated at a differential pressure across the disc as marked on the valve. Lever, worm gear/travelling nut type or any other suitable type of operator can be used. | Satisfactory/Unsatisfactory with details |  | 16.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.1.1 | Direction | Yes | Mandatory | Unless otherwise specified, manually operated valves shall be closed by turning handwheel or lever in a clockwise direction when facing the handwheel or lever. The design of lever when fitted shall be such that the lever may only be assembled to the valve so that it is parallel to the direction of flow when the valve is open. | Satisfactory/Unsatisfactory with details |  | 16.1.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.1.2 | Manual Operation | Yes | Mandatory | All gear travelling nut operators shall be provided with suitable stops to prevent movement of the shaft beyond the limit corresponding to the fully closed position of the disc. | Satisfactory/Unsatisfactory with details |  | 16.1.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.1.3 | Manual Operation | Yes | Mandatory | All gear/travelling nut operators shall be packed with grease for life time operation. Gear/travelling nut operators shall be totally enclosed and whether proof for general application. For special applications such as marine, submerged service, buried service etc. the purchaser may specify special enclosure. | Satisfactory/Unsatisfactory with details |  | 16.1.3 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.1.4 | Manual Operation | Yes | Mandatory | All gear/travelling nut operators shall be self- locking type. All lever operated valve shall be capable of being locked at least three intermediate positions | Satisfactory/Unsatisfactory with details |  | 16.1.4 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Quantitative | 16.1.5 | Manual Operation | Yes | Mandatory | The operating mechanism (lever or gear) shall be designed such that the operator input force applied to the Lever or Hand wheel, required to operate the valve shall not exceed 360 N (36.7 Kg) | Value upto 0 decimal places |  | 16.1.5 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.2 | Manual Operation | Yes | Mandatory | The operating handwheels shall be marked ‘CLOSE’ or ‘SHUT’ to indicate the direction of closure. | Satisfactory/Unsatisfactory with details |  | 16.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.3 | Manual Operation | Yes | Mandatory | The operator shall be provided with arrangement to indicate the disc position. | Satisfactory/Unsatisfactory with details |  | 16.3 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.4.1 | Electric Operators | Yes | Mandatory | Electric motor drives shall be equipped with limit switches and torque switches for both open and closed positions. | Satisfactory/Unsatisfactory with details |  | 16.4.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.4.2 | Electric Operators | Yes | Mandatory | Any gearing in direct association with electric motor drive shall be totally enclosed and shall operate in a lubricant. | Satisfactory/Unsatisfactory with details |  | 16.4.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.4.3 | Electric Operators | Yes | Mandatory | Each electric operator shall be provided with an auxiliary handwheel for manual operation | Satisfactory/Unsatisfactory with details |  | 16.4.3 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.5.1 | Hydraulic Operators | Yes | Mandatory | With cylinder operation, pressure shall be maintained on cylinder piston at each end of its stroke unless other means are provided to prevent drifting. | Satisfactory/Unsatisfactory with details |  | 16.5.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.5.2 | Hydraulic Operators | Yes | Mandatory | Cylinders shall be equipped with dirt wiper to clean the piston rod before it enters the cylinder. | Satisfactory/Unsatisfactory with details |  | 16.5.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.5.3 | Hydraulic Operators | Yes | Mandatory | Rod seals and piston caps shall be of nitrile rubber or other material equally suitable for hydraulic service. | Satisfactory/Unsatisfactory with details |  | 16.5.3 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.6.1 | Pneumatic Operators | Yes | Mandatory | With cylinder operation, pressure shall be maintained on the cylinder piston at each end of its stroke unless other means are provided to prevent drifting | Satisfactory/Unsatisfactory with details |  | 16.6.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.6.2 | Pneumatic Operators | Yes | Mandatory | Cylinders shall be equipped with a dirt wiper to clean the piston rod before it enters the cylinder. Alternatively cylinder with its linkage should be housed in weather-proof enclosure. | Satisfactory/Unsatisfactory with details |  | 16.6.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.6.3 | Pneumatic Operators | Yes | Mandatory | Rod seals, rod wiper and piston caps shall be of neoprene, nitrile rubber or equivalent material suitable for air service. | Satisfactory/Unsatisfactory with details |  | 16.6.3 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.6.4 | Pneumatic Operators | Yes | Mandatory | Cylinders shall be equipped with adjustable cushions at each end of the stroke, if so specified. | Satisfactory/Unsatisfactory with details |  | 16.6.4 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 16.7 | Pneumatic Operators | Yes | Mandatory | When requested by the buyer, the manufacturer shall provide the valve position vs flow resistance curve | Satisfactory/Unsatisfactory with details | Declaration for compliance for providing the valve position vs flow resistance curve | 16.7 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 17 | Testing | No | Mandatory | All valves shall be hydrostatically tested by the manufacturer before dispatch. The pressure shall be obtained without any significant hydraulic shock. Testing shall be carried on before application of paint or other similar treatment unless otherwise agreed between the purchaser and the manufacturer. There shall be no air entrapped within the part of the valves subjected to test pressure. | To be checked on declaration bais | Declaration for compliance to the clause 17 | 17 | 13095 |  |  |  | Test to be carried out by Manufacturer
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 17.1 | Performance Testing | No | Mandatory | Each valve shall be shop operated from fully closed to fully open position and reverse, under no pressure and no flow condition to demonstrate that the complete assembly is workable. | To be checked on declaration bais | Declaration for compliance to the clause 17.1 | 17.1 | 13095 |  |  |  | Test to be carried out by Manufacturer
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 17.2 | Body Test | Yes | Mandatory | Completely assembled valve shall be tested as follows: ‘The body ends shall be blanked so that the valve is subjected to the full pressure in all directions induced by the test pressure. Wafer valves may be tested in any suitable manner agreed between the purchaser and the manufacturer. The valve disc shall be in slightly open position and pressure equivalent to 1.5 times the maximum permissible working pressure shall be applied with water. The duration of this test shall be as in Table 3’ | Satisfactory/Unsatisfactory with details |  | 17.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 17.3.1 | Seat Test | Yes | Mandatory | Each valve shall be shop tested for leaks in closed position. The test shall be conducted with the body flanges in a horizontal position. Pressure shall be applied to the upstream end of the valve, the downstream being open to atmosphere. The duration of test shall be as per Table 3. There shall be no indication of leakage past the valve disc during test and valves shall be drop tight. Seat test shall be carried out in both the directions of valve if agreed between the manufacturer and the purchaser. The seat test pressure applied on upstream side shall be equivalent to 1·1 times the maximum permissible working pressure at 20°C and shall applied with water. | Satisfactory/Unsatisfactory with details |  | 17.3.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Quantitative | 17.3.3 | Seat Test | Yes | Mandatory | Leakage rate, mm3/s | Value upto 1 decimal places | Declaration of Valve Type | 17.3.3 | 13095 | [101 empty] | No visible leakage for duration of test |  | 0.1 mm3/s ×DN |  | Not specified, Outside the scope of this standard
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes | Mechanical | Qualitative | 17.4 | Disc Strength Test | Yes | Mandatory | The test shall be conducted with the body flanges in horizontal position. The test pressure shall be 1·5 times the maximum permissible pressure at 20°C. With disc in closed position, hydro-test pressure shall be applied to the lower face of the disc for duration as per Table 3. There shall be no damage to the valve disc nor shall any part of valve or disc be permanently deformed by the test. The purpose of this test is to provide evidence of the adequacy and structural integrity of disc and body. Any leakage past the seat shall not be the criteria for rejection of the valve (sampling test sample as per IS 2500 (Part 1) : 2000. For regulating type valves, disc strength shall not be applicable. | Satisfactory/Unsatisfactory with details |  | 17.4 | IS 2500 (Part 1) : 2000
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 18 | Test Certificates | No | Optional | When specified by the purchaser, the manufacturer shall issue a test certificate confirming that the valves have been tested in accordance with this standard and starting the actual pressures and medium used in the test. |  |  | 18 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 19 | Inspection | No | Optional | If inspection is required, this shall be stated in the enquiry/order. The purchaser or his authorized representative shall have access to the manufacturer’s works at all reasonable times to inspect assembled valve to his order |  |  | 19 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 20 | Witnessing of Tests | No | Optional | When the purchaser desires to witness the tests, this shall be specifically agreed in advance. |  |  | 20 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 21 | MARKING | Yes | Mandatory | Marking shall be cast integral on the body or on a plate securely attached to the body. The markings shall be in accordance with IS 9866 | To be checked on declaration bais | Declaration for compliance to the clause 21 | 22 | 9866
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 22 | Preparation for dispatch | No | Mandatory | a) Valve shall be complete in all respect when shipped. Each valve shall be drained, cleaned, prepared and suitably protected with 2 coats of red oxide on unmachined surfaces and rust preventive coats on machined and flanged surfaces for dispatch in such a way as to minimize the possibility of damage and deterioration during transit and storage. Painting other than specified on the finished valve shall be as per the agreement between the manufacturer and the purchaser; |  |  | 22 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 22 | Preparation for dispatch | No | Mandatory | Disc shall be unseated when dispatched, but care shall be taken to ensure that there is no risk of damage to the disc; |  |  | 22 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 22 | Preparation for dispatch | No | Mandatory | When specified, the body ends shall be suitably sealed to exclude foreign matter during transit and storage; and |  |  | 22 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 22 | Preparation for dispatch | No | Mandatory | Components shipped unattached shall be adequately protected and identified to permit correct field assembly. |  |  | 22 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 23.1 | Information to be furnished by the purchaser in an order of enquiry | No | Mandatory | General Requirements |  |  | 23.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 23..1.1 | Information to be furnished by the purchaser in an order of enquiry | No | Mandatory | Service |  |  | 23..1.1 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 23.1.2 | Information to be furnished by the purchaser in an order of enquiry | No | Mandatory | Mode of Operation |  |  | 23.1.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 23.1.3 | Information to be furnished by the purchaser in an order of enquiry | No | Mandatory | Type of construction |  |  | 23.1.3 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 23.2 | Information to be furnished by the purchaser in an order of enquiry | No | Mandatory | Special requirements like spool pieces, floor stands, etc |  |  | 23.2 | 13095
13095 | 0 | 0 | 2020 | 2 | Butterfly Valves for General Purposes |  | Qualitative | 23.3 | Information to be furnished by the purchaser in an order of enquiry | No | Mandatory | Any other information not covered in the above sections. |  |  | 23.3 | 13095

## 13095 TReq
Grade | Material type | End Connnection | Declaration of valve application | Size - Nominal size of valve | Category | Declared Value 1 - Nominal Pressure | Declared Value 2 - Material of Flange | Declared Value 3 - Pressure Class | Declared Value 4 - Material of Various Parts | Declaration of valve end connections as per Fig. 1 / 2 / 3 / 4 / 5 / 6 | Declaration of nominal size | Declaration of nominal pipe size | Declaration of class | Declaration of material | Declaration of specified requirements | Declaration of Material Declaration of Nominal Pressure Declaration if material to be tested as per IS 6418, IS 6392, and IS 9523 | Declaration whether material is to be tested as per IS 13159 (Part 1) | Declaration of compliance with pressure/temperature ratings | Declaration whether flanges are drilled | Declaration for compliance with valve position versus flow resistance curve | Declaration for compliance with Clause 17 | Declaration for compliance with Clause 21
| cast iron | flanged | Tight shut-off | 40 |  | PN 0.25 | Integral Grey Cast Iron Flanges | Class 125 | Material of Body
| ductile iron | wafer | Low leakage | 50 |  | PN 0.60 | Malleable Cast Iron Integral Flanges | Class 150 | Material of Disc
| carbon steel |  | Regulating | 65 |  | PN 1.0 | Ductile Iron Integral Flanges | Class 300 | Material of Shaft
| stainless steel |  |  | 80 |  | PN 1.6 | Steel Plate Flanges for Welding |  | Material of Seating ring/Seal retaining ring
| aluminium |  |  | 100 |  | PN 2.5 | Integral Steel Flanges |  | Material of Seat
|  |  |  | 125 |  | PN 4.0 |  |  | Material of Shaft bearing seals
|  |  |  | 150 |  |  |  |  | Material of Internal fastenings
|  |  |  | 200 |  |  |  |  | Material of External bolting
250
300
350
400
450
500
600
700
800
900
1000
1200
1400
1600
1800
2000
Note on I1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Delete it, see Amendment no.2