## Sheet1
[21 empty] | Thickness of Insulation | [42 empty] | Conductor Resistance Solid Conductors for Single Core and Multicore Cables (Class-1), Plain Copper Conductor | [24 empty] | Conductor Resistance Solid Conductors for Single Core and Multicore Cables (Class-1), Tinned Copper Conductor | [12 empty] | Conductor Resistance Solid Conductors for Single Core and Multicore Cables (Class-1), Aluminium Conductor | [31 empty] | Conductor Resistance Stranded conductors for Single Core and Multicore Cables (Class-2), Plain Copper Conductor | [41 empty] | Conductor Resistance Stranded conductors for Single Core and Multicore Cables (Class-2), Tinned Copper Conductor | [41 empty] | Conductor Resistance Stranded conductors for Single Core and Multicore Cables (Class-2), Aluminium Conductor | [40 empty] | Thickness of Inner Sheath, Calculated Diameter Over Laid-up Cores (Ref IS 10462 Part 1) | [9 empty] | Thickness of outer Sheath, Calculated Diameter Under Outer Sheath (Ref IS 10462 Part 1) | [23 empty] | Physical test for Sheath, Type of Sheath | [7 empty] | Calculated Diameter Underthe Armour (Ref IS 10462 Part 1) |  | Calculated Diameter Underthe Armour (Ref IS 10462 Part 1) | [40 empty] | Wire Diameter
IS Number | Part | Section | Year | Number of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause/ Table/ Annex Reference | Test Parameter Name | To be tested and/or reported by Lab (YES / NO) | Mandatory or Optional | Characteristics (as per Indian Standard) - No specified values to be mentioned here | Test Result/ Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference | Sample Quantity | Equipment |  | Specified limits for size 1.5 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 4 mm2 | Specified limits for size 4 mm2 | Specified limits for size 6 mm2 | Specified limits for size 6 mm2 | Specified limits for size 10 mm2 | Specified limits for size 10 mm2 | Specified limits for size 16 mm2 | Specified limits for size 16 mm2 | Specified limits for size 25 mm2 | Specified limits for size 25 mm2 | Specified limits for size 35 mm2 | Specified limits for size 35 mm2 | Specified limits for size 50 mm2 | Specified limits for size 50 mm2 | Specified limits for size 70 mm2 | Specified limits for size 70 mm2 | Specified limits for size 95 mm2 | Specified limits for size 95 mm2 | Specified limits for size 120 mm2 | Specified limits for size 120 mm2 | Specified limits for size 150 mm2 | Specified limits for size 150 mm2 | Specified limits for size 185 mm2 | Specified limits for size 185 mm2 | Specified limits for size 240 mm2 | Specified limits for size 240 mm2 | Specified limits for size 300 mm2 | Specified limits for size 300 mm2 | Specified limits for size 400 mm2 | Specified limits for size 400 mm2 | Specified limits for size 500 mm2 | Specified limits for size 500 mm2 | Specified limits for size 630 mm2 | Specified limits for size 630 mm2 | Specified limits for size 800 mm2 | Specified limits for size 800 mm2 | Specified limits for size 1000 mm2 | Specified limits for size 1000 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 4 mm2 | Specified limits for size 4 mm2 | Specified limits for size 6 mm2 | Specified limits for size 6 mm2 | Specified limits for size 10 mm2 | Specified limits for size 10 mm2 | Specified limits for size 16 mm2 | Specified limits for size 16 mm2 | Specified limits for size 25 mm2 | Specified limits for size 25 mm2 | Specified limits for size 35 mm2 | Specified limits for size 35 mm2 | Specified limits for size 50 mm2 | Specified limits for size 50 mm2 | Specified limits for size 70 mm2 | Specified limits for size 70 mm2 | Specified limits for size 95 mm2 | Specified limits for size 95 mm2 | Specified limits for size 120 mm2 | Specified limits for size 120 mm2 | Specified limits for size 150 mm2 | Specified limits for size 150 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 4 mm2 | Specified limits for size 4 mm2 | Specified limits for size 6 mm2 | Specified limits for size 6 mm2 | Specified limits for size 10 mm2 | Specified limits for size 10 mm2 | Specified limits for size 16 mm2 | Specified limits for size 16 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 4 mm2 | Specified limits for size 4 mm2 | Specified limits for size 6 mm2 | Specified limits for size 6 mm2 | Specified limits for size 10 mm2 | Specified limits for size 10 mm2 | Specified limits for size 16 mm2 | Specified limits for size 16 mm2 | Specified limits for size 25 mm2 | Specified limits for size 25 mm2 | Specified limits for size 35 mm2 | Specified limits for size 35 mm2 | Specified limits for size 50 mm2 | Specified limits for size 50 mm2 | Specified limits for size 70 mm2 | Specified limits for size 70 mm2 | Specified limits for size 95 mm2 | Specified limits for size 95 mm2 | Specified limits for size 120 mm2 | Specified limits for size 120 mm2 | Specified limits for size 150 mm2 | Specified limits for size 150 mm2 | Specified limits for size 185 mm2 | Specified limits for size 185 mm2 | Specified limits for size 240 mm2 | Specified limits for size 240 mm2 | Specified limits for size 300 mm2 | Specified limits for size 300 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 4 mm2 | Specified limits for size 4 mm2 | Specified limits for size 6 mm2 | Specified limits for size 6 mm2 | Specified limits for size 10 mm2 | Specified limits for size 10 mm2 | Specified limits for size 16 mm2 | Specified limits for size 16 mm2 | Specified limits for size 25 mm2 | Specified limits for size 25 mm2 | Specified limits for size 35 mm2 | Specified limits for size 35 mm2 | Specified limits for size 50 mm2 | Specified limits for size 50 mm2 | Specified limits for size 70 mm2 | Specified limits for size 70 mm2 | Specified limits for size 95 mm2 | Specified limits for size 95 mm2 | Specified limits for size 120 mm2 | Specified limits for size 120 mm2 | Specified limits for size 150 mm2 | Specified limits for size 150 mm2 | Specified limits for size 185 mm2 | Specified limits for size 185 mm2 | Specified limits for size 240 mm2 | Specified limits for size 240 mm2 | Specified limits for size 300 mm2 | Specified limits for size 300 mm2 | Specified limits for size 400 mm2 | Specified limits for size 400 mm2 | Specified limits for size 500 mm2 | Specified limits for size 500 mm2 | Specified limits for size 630 mm2 | Specified limits for size 630 mm2 | Specified limits for size 800 mm2 | Specified limits for size 800 mm2 | Specified limits for size 1000 mm2 | Specified limits for size 1000 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 4 mm2 | Specified limits for size 4 mm2 | Specified limits for size 6 mm2 | Specified limits for size 6 mm2 | Specified limits for size 10 mm2 | Specified limits for size 10 mm2 | Specified limits for size 16 mm2 | Specified limits for size 16 mm2 | Specified limits for size 25 mm2 | Specified limits for size 25 mm2 | Specified limits for size 35 mm2 | Specified limits for size 35 mm2 | Specified limits for size 50 mm2 | Specified limits for size 50 mm2 | Specified limits for size 70 mm2 | Specified limits for size 70 mm2 | Specified limits for size 95 mm2 | Specified limits for size 95 mm2 | Specified limits for size 120 mm2 | Specified limits for size 120 mm2 | Specified limits for size 150 mm2 | Specified limits for size 150 mm2 | Specified limits for size 185 mm2 | Specified limits for size 185 mm2 | Specified limits for size 240 mm2 | Specified limits for size 240 mm2 | Specified limits for size 300 mm2 | Specified limits for size 300 mm2 | Specified limits for size 400 mm2 | Specified limits for size 400 mm2 | Specified limits for size 500 mm2 | Specified limits for size 500 mm2 | Specified limits for size 630 mm2 | Specified limits for size 630 mm2 | Specified limits for size 800 mm2 | Specified limits for size 800 mm2 | Specified limits for size 1000 mm2 | Specified limits for size 1000 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 1.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 2.5 mm2 | Specified limits for size 4 mm2 | Specified limits for size 4 mm2 | Specified limits for size 6 mm2 | Specified limits for size 6 mm2 | Specified limits for size 10 mm2 | Specified limits for size 10 mm2 | Specified limits for size 16 mm2 | Specified limits for size 16 mm2 | Specified limits for size 25 mm2 | Specified limits for size 25 mm2 | Specified limits for size 35 mm2 | Specified limits for size 35 mm2 | Specified limits for size 50 mm2 | Specified limits for size 50 mm2 | Specified limits for size 70 mm2 | Specified limits for size 70 mm2 | Specified limits for size 95 mm2 | Specified limits for size 95 mm2 | Specified limits for size 120 mm2 | Specified limits for size 120 mm2 | Specified limits for size 150 mm2 | Specified limits for size 150 mm2 | Specified limits for size 185 mm2 | Specified limits for size 185 mm2 | Specified limits for size 240 mm2 | Specified limits for size 240 mm2 | Specified limits for size 300 mm2 | Specified limits for size 300 mm2 | Specified limits for size 400 mm2 | Specified limits for size 400 mm2 | Specified limits for size 500 mm2 | Specified limits for size 500 mm2 | Specified limits for size 630 mm2 | Specified limits for size 630 mm2 | Specified limits for size 800 mm2 | Specified limits for size 800 mm2 | Specified limits for size 1000 mm2 | Specified limits for size 1000 mm2 | Upto 25 | Upto 25 | 25-35 | 25-35 | 35-45 | 35-45 | 45-55 | 45-55 | 55- Above | 55- Above | Upto 15 | Upto 15 | 15-25 | 15-25 | 25-35 | 25-35 | 35-40 | 35-40 | 40-45 | 40-45 | 45-50 | 45-50 | 50-55 | 50-55 | 55-60 | 55-60 | 60-65 | 60-65 | 65-70 | 65-70 | 70-75 | 70-75 | 75-85 | 75-85 | ST2 |  | PE |  | ST8 |  | ST12 |  | For all diameters in excess of 13 | For all diameters in excess of 13 | Upto 13 | Upto 13 | 13-25 | 13-25 | 25-40 | 25-40 | 40-55 | 40-55 | 55-70 | 55-70 | Above 70 | Above 70 | Calculated Diameter Under Armour, For all diameter in excess of 13 mm, Min | Calculated Diameter Under Armour, For all diameter in excess of 13 mm, Max | Calculated Diameter, upto 13 mm, Min | Calculated Diameter, upto 13 mm, Max | Calculated Diameter, Over 13 mm including upto 25 mm, Min | Calculated Diameter, Over 13 mm including upto 25 mm, Max | Calculated Diameter, Over 25 mm including upto 40 mm, Min | Calculated Diameter, Over 25 mm including upto 40 mm, Max | Calculated Diameter, Over 40 mm including upto 55 mm, Min | Calculated Diameter, Over 40 mm including upto 55 mm, Max | Calculated Diameter, Over 55 mm including upto 70 mm, Min | Calculated Diameter, Over 55 mm including upto 70 mm, Max | Calculated Diameter, Over 70 mm, Min | Calculated Diameter, Over 70 mm, Max | Wire Diameter, Up to and Including 0.21 mm, Min | Wire Diameter, Up to and Including 0.21 mm, Max | Wire Diameter,over 0.21 Up to and Including 0.41 mm, Min | Wire Diameter,over 0.21 Up to and Including 0.41 mm, Max | Wire Diameter,over 0.41 Up to and Including 1.36 mm, Min | Wire Diameter,over 0.41 Up to and Including 1.36 mm, Max | Wire Diameter,over 1.36 mm, Min | Wire Diameter,over 1.36 mm, Max | Grade 0, Min | Grade 0, Max | Grade H2, Min | Grade H2, Max | Grade H4, Min | Grade H4, Max | Up to and including 0.41 mm | Up to and including 0.41 mm | Above 0.41 mm | Above 0.41 mm | Min | Max | Specified limits for XXXX 1 | Specified limits for XXXX 1 | Specified limits for XXXX 2 | Specified limits for XXXX 2 | Specified limits for XXXX 3 | Specified limits for XXXX 3 | If the test is quantitative, the Min and Max value to be written after applying the tolerance given in the standard. If only upper and lower limit is given, mention ONLY Min or ONLY Max balue and leave the other cell blank. If the test is Qualitative, both Only Min column to be filled by the qualitiative requirement, the Max column to be left blank
THIS ROW TO BE LEFT BLANK | [20 empty] | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | [28 empty] | Min | Max | Min | Max |  |  | Min | Max | Min | Max | Min | Max
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 4.1 | Conductor material (Aluminium) | Yes | Mandatory | The material for conductor shall consist of plain aluminium. It shall be one of the 0, H2 or H4 grades. (Cl. 4.1 of IS 8130:2013) | To be checked based on declaration basis | Material of conductor | Cl. 4.1 | IS 8130 | To be only filled if the Column I and Column J are having same information and Column M is having different information | NOT TO BE FILLED
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 4.1 | Conductor material (Copper) | Yes | Mandatory | The conductors shall consist of Plain copper as may be specified. (Cl. 4.2 of IS 8130:2013) | To be checked based on declaration basis | Material of conductor | Cl. 4.2 | IS 8130
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 4.2 | Conductor Material | Yes | Mandatory | Mining cables to be used in gassy mines shall be of copper conductor only, | To be checked based on declaration basis | Material of conductor |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 4.2 | Conductor Material | Yes | Mandatory | Tinned copper conductors can be used on agreement between manufacture and purchaser | To be checked based on declaration basis | Material of conductor |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Cl. 4.1 | Form of conductor | Yes | Mandatory | The conductors shall be solid, circular, shaped, compacted, stranded or bunched as required by the appropriate cable specification | Satisfactory/ Unsatisfactory (solid/ circular/ shaped/ compacted/ stranded/ bunched ) | Form of conductor | Cl. 4.3 | IS 8130
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.1 a) | Core Identification | Yes | Mandatory | For identification by using colured strips Red, Yellow, Blue Colour shall be use for phase Conductors and Black to identied reduced netural conductor | Satisfactory/ Unsatisfactory (Red, Yellow, Blue ,Black) |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.1 b) 1) | Core Identification (Single core) | Yes | Mandatory | Colouring of XLPE Insulation as follows; Single core- Red, black, yellow, blue, or Natural | Satisfactory/ Unsatisfactory (Colour of core) |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.1 b) 2) | Core Identification (Two core) | Yes | Mandatory | Colouring of XLPE Insulation as follows; Two core- Red, black | Satisfactory/ Unsatisfactory (Colour of core) ( 2 Observations) |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.1 b) 3) | Core Identification (Three core) | Yes | Mandatory | Colouring of XLPE Insulation as follows; Three core- Red, Yellow and Blue | Satisfactory/ Unsatisfactory (Colour of core) ( 3 Observations) |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.1 b) 4) | Core Identification (Four core) | Yes | Mandatory | Colouring of XLPE Insulation as follows; Four core- Red, Yellow, Blue and Black | Satisfactory/ Unsatisfactory (Colour of core) ( 4 Observations) |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.1 b) 5) | Core Identification (Five core) | Yes | Mandatory | Colouring of XLPE Insulation as follows; Five core- Red, Yellow, Blue Black and Grey | Satisfactory/ Unsatisfactory (Colour of core) ( 5 Observations) |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.1 b) 6) | Core Identification (Six cores and Above) | Yes | Mandatory | Two adjacent cores (counting and direction core) in each layer, blue and yellow, remaining cores, grey | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.1 c) 1) | Core Identification (Two core) | Yes | Mandatory | By numerals either by applying numbered strips or by printing on the cores as follows as: Two core- 0 and 1 | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.1 c) 2) | Core Identification (Three core) | Yes | Mandatory | By numerals either by applying numbered strips or by printing on the cores as follows as: Three core-0 , 1 and 2 | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.1 c) 3) | Core Identification (Four core) | Yes | Mandatory | By numerals either by applying numbered strips or by printing on the cores as follows as: Four core-0 , 1 , 2 and 3 | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.2, 11.4 | Core Identification (Reduced neutral) | Yes | Mandatory | For reduced neutral conductors, the core shall be black. For reduced neutral conductors, the core shall have ‘0’ number | Satisfactory/ Unsatisfactory/NA |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 11.3 | Core Identification (Cables having more than four cores)) | Yes | Mandatory | For cables having more than 4 cores, as an alternative to the provision of 11.1 the core identification may be done by numbers | Satisfactory/ Unsatisfactory/NA |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 5 | Insulation | Yes | Mandatory | The conductor (With protective barrier wherever applied) shall be provided with XLPE Insulation applied by extrusion | Satisfactory/ Unsatisfactory/NA |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 10.4 | Application of Insulation | Yes | Mandatory | The insulation shall be so applied that it fits closely on the conductor (or barrier if any) and it shall be possible to remove it without damaging the conductor. | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 6.1 | Filler and Inner Sheath | Yes | Mandatory | The fillers and inner sheath shall be of the following: a) Vulcanized or unvulcanized rubber; and b) Thermoplastic materials | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 6.2 | Filler and Inner Sheath | Yes | Mandatory | The vulcanized or unvulcanized rubber or thermoplastic materials used for inner sheath shall not be harder than insulation and outer sheath respectively. Fillers and inner sheath materials shall be so chosen as to be compatible with the temperature ratings of the cable and shall have no deleterious effect on any other component of the cable. | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 6.3 | Filler and Inner Sheath | Yes | Mandatory | Materials used for fillers and inner sheath in case of LSHF cables shall be halogen free and comply with sl no. (v) of Table 1B | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 13.1 | Inner Sheath ( Common Covering) | Yes | Mandatory | The laid-up cores shall be provided with an inner sheath applied either by extrusion or by wrapping. It shall be ensured that it is as circular as possible. | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 13.2 | Inner Sheath ( Common Covering) | Yes | Mandatory | The inner sheath shall be so applied that it fits closely on the laid-up cores and it shall be possible to remove it without damage to the insulation | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 13.3 | Inner Sheath ( Common Covering) | Yes | Mandatory | Thickness of inner sheath-the thickness of inner sheath (common covering) shall be as given in Table 5. Single core cables shall have no inner sheath. When one or more layers of proofed or plastic tape are applied over the laid-up cores as a binder, the thickness of such tapes shall not be construed as part of extruded inner sheath. (unit : mm) | (Value upto 1 decimal places) |  |  | IS 7098 part 1 | [242 empty] | 0.3 |  | 0.4 |  | 0.5 |  | 0.6 |  | 0.7
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 7.1 | Armouring | Yes | Mandatory | Armouring shall be of the following: a) Galvanized round steel wire; b) Galvanized formed steel wire (strip); and c) Any metallic non-magnetic wire/strip. | Satisfactory/ Unsatisfactory | Declaration regarding Armour type |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 7.2, 14.6 | Armouring | Yes | Mandatory | The requirement of non-magnetic materials shall be as agreed between purchaser and supplier. | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 14.1.1 | Armouring Application | Yes | Mandatory | Armouring shall be applied over the insulation in case of single core cables and over the inner sheath in case of twin, three and multi core cables. | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.1.2 | Armouring Coverage | Yes | Mandatory | The armour round wires/formed wires shall be applied as closely as practicable with a coverage. (unit : %), Min | Whole Number | Declaration regarding Armour type |  | IS 7098 part 1 | [330 empty] | 90
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 14.1.3 | Armouring Direction of lay | Yes | Mandatory | The direction for lay of the armour shall be left hand. For double round wire/formed wire armoured cables, this requirement shall apply to the inner layer of round wires/formed wires. | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 14.1.3 | Armouring Direction of lay | Yes | Mandatory | The outer layer shall, except in special cases, be applied in the reverse direction to the inner layer, and there shall be a separator of suitable non-hygroscopic material . | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 14.1.4 | Armouring | Yes | Mandatory | A binder tape may be provided on the armour | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 14.2 | Type of Armour | Yes | Mandatory | Where the calculated diameter below armouring does not exceed 13 mm, the armour shall consist of round wires.(unit : mm) | Satisfactory/ Unsatisfactory | Declaration regarding Armour type |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 14.2 | Type of Armour | Yes | Mandatory | Where the calculated diameter below armouring is greater than 13 mm, the armour shall consist of either round steel wires /formed wires.(unit : mm) | Satisfactory/ Unsatisfactory | Declaration regarding Armour type |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.3 | Armour Dimension (Nominal thickness of formed wire) A: | Yes | Mandatory | Armour Dimension, mm, Max | (Value upto 1 decimal places) |  |  | IS 10810 Part 36 | [284 empty] | 4 |  |  |  | 4 |  | 4 |  | 6.1 |  | 6.1 |  | 6.1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.3 | Armour Dimension (Nominal thickness of formed wire) C: | Yes | Mandatory | Armour Dimension, mm, Max | (Value upto 1 decimal places) |  |  | IS 10810 Part 36 | [284 empty] | 0.8 |  |  |  | 0.8 |  | 0.8 |  | 1.4 |  | 1.4 |  | 1.4
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.3 | Armour Dimension (Nominal Diameter of Round wire) | Yes | Mandatory | Armour Dimension, mm, Max | (Value upto 1 decimal places) |  |  | IS 10810 Part 36 | [286 empty] | 1.4 |  | 1.6 |  | 2 |  | 2.5 |  | 3.15 |  | 4
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 14.4 | Armour Joints | Yes | Mandatory | The joints in armour wires shall be made by brazing or welding and the surface irregularities shall be removed. A joint in any wire/strip shall be at least 300 mm from the nearest joint in any other armour wire/strip in the completed cable | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.5.1 | Armour Resistance | Yes | Mandatory | Armour Resistance, (unit : Ω/km), Max | (Value upto 3 decimal places) | DC resistance of armour |  | IS 10810 Part 5
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.5.2 | Armour Resistance | Yes | Mandatory | In case of cables for use in mines, the resistance of armour shall not exceed that of the conductor as specified in IS 8130 by more than 33 percent.(unit : Ω/km) | (Value upto 3 decimal places) | Size of Armour |  | IS 10810 Part 5
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.6 a) | Armour Tensile Strength | Yes | Mandatory | The tensile strength of rounds steel wire/formed steel wire, (unit : N/mm2) | Whole Number |  |  | IS 10810 Part 37 | [330 empty] | 250 | 580
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.6 b) | Armour Elongation | Yes | Mandatory | The elongation at break of round steel wire/formed steel wire, (unit : %), Min | Whole Number |  |  | IS 10810 Part 37 | [330 empty] | 6
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.6 c) | Armour Torsion | Yes | Mandatory | Number of turns without break, Min | Whole Number |  |  | IS 10810 Part 38 | [300 empty] | 43 |  | 37 |  | 30 |  | 24 |  | 19 |  | 15
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 14.6 d) | Armour Winding Test | Yes | Mandatory | The zinc coating shall not show any cracks and shall not flake off on robbing by the bare finger when the formed steel wire is subjected to winding test | Satisfactory/ Unsatisfactory |  |  | IS 10810 Part 39
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 14.6 e) | Armour Uniformity of zinc | Yes | Mandatory | The uniformity of zinc coating of round steel wire/formed steel wire shall comply with the requirements of IS 3975 subject to the following; | Satisfactory/ Unsatisfactory |  |  | IS 10810 Part 40
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.6 f) | Armour Mass of zinc coating Round wire | Yes | Mandatory | The mass of zinc coating of round steel wire, (unit : g/m2), Min | (Value upto 1 decimal places) |  |  | IS 10810, Part 41
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.6 g) | Armour Mass of zinc coating formed wire | Yes | Mandatory | The mass of zinc coating of formed steel wire, (unit : g/m2), Min | (Value upto 1 decimal places) |  |  | IS 10810, Part 41
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 3, Clause 14.6 h) | Armour Resistivity | Yes | Mandatory | Armour Resistivity, Max, (unit : Ohm-cm). | (Value upto 1 decimal places X 10^6) |  |  | IS 10810 Part 42 | [331 empty] | 14.5 x 10^6
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 2, Clause 8.1 | Outer Sheath | Yes | Mandatory | The outer sheath shall be of polyvinyl chloride (PVC) compound or thermoplastic polyethylene (PE) compound or thermoplastic low smoke and halogen free (LSHF) compound | Satisfactory/ Unsatisfactory | Type of outer sheath |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 15.1 | Outer Sheath Application | Yes | Mandatory | The outer sheath shall be applied by extrusion. It shall be applied: a) Over the insulation in case of unarmoured single core cables; b) Over the inner sheath in case of unarmoured twin, three and multicore cables; and c) Over armouring in case of armoured cables | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 3, Clause 15.2 | Outer Sheath | Yes | Mandatory | The colour of outer sheath shall be black or any other colour as agreed to between purchaser and supplier | Satisfactory/ Unsatisfactory |  |  | IS 7098 part 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 4, 16.1 (i) a) | Annealing Test (for copper) | Yes | Mandatory | Elongation, Min, (Unit : %) | (Value upto 1 decimal places) |  |  | IS 10810 Part 1 | [312 empty] | 9 |  | 13.5 |  | 18 |  | 22.5
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 4, 16.1 (i) b) | Tensile Test (for aluminium conductor before stranding) | Yes | Mandatory | Tensile Strength, Min, (Unit:N/mm2) | (Value upto 1 decimal places) | Conductor grade (0/H2/H4) |  | IS 10810 Part 2 | [320 empty] | 0 | 100 | 100 | 150 | 150
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 4, 16.1 (i) b) | Tensile Test (for aluminium conductor after stranding) | Yes | Mandatory | Tensile Strength, Min, (Unit:N/mm2) | (Value upto 1 decimal places) | Conductor grade (0/H2/H4) |  | IS 10810 Part 2 | [320 empty] | 0 | 95 | 95 | 142.5 | 142.5
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Section 4, 16.1 (i) c) | Wrapping Test (for aluminium) | Yes | Mandatory | The conductor shall be composed of aluminum wires complying with IS 8130.The cretia of passing is that the conductor shall not break. | Satisfactory/ Unsatisfactory (Break) |  |  | IS 10810 Part 3
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Section 4, 16.1 (i) d), | Conductor resistance test | Yes | Mandatory | Conductor resistance, Max,(Unit:ohm/km) | (Value upto 3 decimal places) |  |  | IS 10810 Part 5 |  |  |  | Number of observations is equal to Number of Cores | [43 empty] | 12.1 |  | 7.41 |  | 4.61 |  | 3.08 |  | 1.83 |  | 1.15 |  | 0.727 |  | 0.524 |  | 0.387 |  | 0.268 |  | 0.193 |  | 0.153 |  | 0.124 |  | 12.2 |  | 7.56 |  | 4.7 |  | 3.11 |  | 1.84 |  | 1.16 |  | 18.1 |  | 12.1 |  | 7.41 |  | 4.61 |  | 3.08 |  | 1.91 |  | 1.2 |  | 0.868 |  | 0.641 |  | 0.443 |  | 0.32 |  | 0.253 |  | 0.206 |  | 0.164 |  | 0.125 |  | 0.1 |  | 12.1 |  | 7.41 |  | 4.61 |  | 3.08 |  | 1.83 |  | 1.15 |  | 0.727 |  | 0.524 |  | 0.387 |  | 0.268 |  | 0.193 |  | 0.153 |  | 0.124 |  | 0.0991 |  | 0.0754 |  | 0.0601 |  | 0.047 |  | 0.0366 |  | 0.0283 |  | 0.0221 |  | 0.0176 |  | 12.2 |  | 7.56 |  | 4.7 |  | 3.11 |  | 1.84 |  | 1.16 |  | 0.734 |  | 0.529 |  | 0.391 |  | 0.27 |  | 0.195 |  | 0.154 |  | 0.126 |  | 0.1 |  | 0.0762 |  | 0.0607 |  | 0.0475 |  | 0.0369 |  | 0.0286 |  | 0.0224 |  | 0.0177 |  | 18.1 |  | 12.1 |  | 7.41 |  | 4.61 |  | 3.08 |  | 1.91 |  | 1.2 |  | 0.868 |  | 0.641 |  | 0.443 |  | 0.32 |  | 0.253 |  | 0.206 |  | 0.164 |  | 0.125 |  | 0.1 |  | 0.0778 |  | 0.0605 |  | 0.0469 |  | 0.0367 |  | 0.0291
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 4.2 | Persulphate Test (for tinned copper conductor) | Yes | Mandatory | Persulphate Test, Max.(Unit:g/m2) | Whole Number |  |  | IS 10810 Part 4 | [327 empty] | 5 |  | 3
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Dimensional | Quantitative | Clause 10.2, Table 3, Section 4, 16.1 (iii) | Thickness of Insulation, Single core Armoured Cables (Nominal) | Yes | Mandatory | The mean value of the thickness of insulation, Min, (Unit : mm) | (Value upto 2 decimal places) | Size of Cable |  | IS 10810 Part 6 |  |  |  | Number of observations is equal to Number of Cores, Measured value in mm upto 3 decimal place and average of 18 readings on 3 specimens at 6 locations. | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1.2 |  | 1.2 |  | 1.3 |  | 1.4 |  | 1.4 |  | 1.5 |  | 1.7 |  | 1.9 |  | 2 |  | 2.1 |  | 2.4 |  | 2.6 |  | 2.8 |  | 3.1 |  | 3.3
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 10.3, Table 3 Section 4, 16.1 (iii) | Thickness of Insulation, Single core Armoured Cables (Minimum) | Yes | Mandatory | The smallest of the measured values of thickness of insulation (ti ) shall not fall below the nominal value (t i ) specified in the relevant table by more than (0.1 mm +0.1 ti ), Min. (Unit : mm) | (Value upto 2 decimal places) | Size of Cable |  | IS 10810 Part 6 |  |  |  | Number of observations is equal to Number of Cores, Measured value in mm upto 3 decimal place and average of 18 readings on 3 specimens at 6 locations. | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.98 |  | 0.98 |  | 1.07 |  | 1.16 |  | 1.16 |  | 1.25 |  | 1.43 |  | 1.61 |  | 1.7 |  | 1.79 |  | 2.06 |  | 2.24 |  | 2.42 |  | 2.69 |  | 2.87
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Dimensional | Quantitative | Clause 10.3, Table 3 Section 4, 16.1 (iii) | Thickness of Insulation, Single core Un-Armoured and Multi-core Cables (Nominal) | Yes | Mandatory | The mean value of the thickness of insulation shall be not less than the specified value for each type and size of cable shown in the relevant tables given in Section 2 and Section 3.Min. (Unit : mm) | (Value upto 2 decimal places) | Size of Cable |  | IS 10810 Part 6 |  |  |  | Number of observations is equal to Number of Cores, Measured value in mm upto 3 decimal place and average of 18 readings on 3 specimens at 6 locations. | 0.7 |  | 0.7 |  | 0.7 |  | 0.7 |  | 0.7 |  | 0.7 |  | 0.9 |  | 0.9 |  | 1 |  | 1.1 |  | 1.1 |  | 1.2 |  | 1.4 |  | 1.6 |  | 1.7 |  | 1.8 |  | 2 |  | 2.2 |  | 2.4 |  | 2.6 |  | 2.8
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 10.3, Table 3 Section 4, 16.1 (iii) | Thickness of Insulation, Single core Un-Armoured and Multi-core Cables (Minimum) | Yes | Mandatory | The smallest of the measured values of thickness of insulation (ti ) shall not fall below the nominal value (t i ) specified in the relevant table by more than (0.1 mm +0.1 ti ), Min, (Unit : mm) | (Value upto 2 decimal places) | Size of Cable |  | IS 10810 Part 6 |  |  |  | Number of observations is equal to Number of Cores, Measured value in mm upto 3 decimal place and average of 18 readings on 3 specimens at 6 locations. | 0.53 |  | 0.53 |  | 0.53 |  | 0.53 |  | 0.53 |  | 0.53 |  | 0.71 |  | 0.71 |  | 0.8 |  | 0.89 |  | 0.89 |  | 0.89 |  | 1.16 |  | 1.34 |  | 1.43 |  | 1.52 |  | 1.7 |  | 1.88 |  | 2.06 |  | 2.24 |  | 2.42
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 15.3, Table 7 Section 4, 16.1 (iii) | Thickness of Outer Sheath for Un-Armoured Cables (Nominal) | Yes | Mandatory | The mean value of the thickness of sheath shall be not less than the specified value for each type and size of cable shown in the relevant tables given in ISS, Min. (Unit : mm) | (Value upto 2 decimal places) | Size of Cable |  | IS 10810 Part 6 |  |  |  | Number of observations is equal to Number of Cores, Measured value in mm upto 3 decimal place and average of 18 readings on 3 specimens at 6 locations. | [248 empty] | 1.8 |  | 2 |  | 2.2 |  | 2.4 |  | 2.6 |  | 2.8 |  | 3 |  | 3.2 |  | 3.4 |  | 3.6 |  | 3.8 |  | 4
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 15.3, Table 7 Section 4, 16.1 (iii) | Thickness of Outer Sheath for Un-Armoured Cables (Minimum) | Yes | Mandatory | The smallest of the measured values of thickness of sheath (ti ) shall not fall below the minimum value specified in the relevant table, Min, (Unit : mm) | (Value upto 2 decimal places) | Size of Cable |  | IS 10810 Part 6 |  |  |  | Number of observations is equal to Number of Cores, Measured value in mm upto 3 decimal place and average of 18 readings on 3 specimens at 6 locations. | [248 empty] | 1.24 |  | 1.4 |  | 1.56 |  | 1.72 |  | 1.88 |  | 2.04 |  | 2.2 |  | 2.36 |  | 2.52 |  | 2.68 |  | 2.84 |  | 3
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 15.3, Table 7 Section 4, 16.1 (iii) | Thickness of Outer Sheath for Armoured Cables (Minimum) | Yes | Mandatory | The smallest of the measured values of thickness of sheath (ti ) shall not fall below the minimum value specified in the relevant table, Min, (Unit : mm) | (Value upto 2 decimal places) | Size of Cable |  | IS 10810 Part 6 |  |  |  | Number of observations is equal to Number of Cores, Measured value in mm upto 3 decimal place and average of 18 readings on 3 specimens at 6 locations. | [248 empty] | 1.24 |  | 1.4 |  | 1.56 |  | 1.72 |  | 1.88 |  | 2.04 |  | 2.2 |  | 2.36 |  | 2.52 |  | 2.68 |  | 2.84 |  | 3
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 13.3, Table 5 Section 4, 16.1 (iii) | Thickness of Inner Sheath (Minimum) | Yes | Mandatory | The smallest of the measured values of thickness of sheath (ti ) shall not fall below the minimum value specified in the relevant table, Min, (Unit : mm) | (Value upto 2 decimal places) | Size of Cable |  | IS 10810 Part 6 |  |  |  | Number of observations is equal to Number of Cores, Measured value in mm upto 3 decimal place and average of 18 readings on 3 specimens at 6 locations. | [238 empty] | 0.3 |  | 0.4 |  | 0.5 |  | 0.6 |  | 0.7
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 5 , 16.1, and 16.2, Table 1 , i) Section 4, 16.1 (iv) a) | Physical test for insulation-Tensile Strength at break (Without agenig) | Yes | Mandatory (Acceptance) | Tensile Strength, Min, (Unit : N/mm2) | (Value upto 1 decimal places) |  |  | IS 10810 Part 7 | [330 empty] | 12.5
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 5 , 16.1, and 16.2, Table 1 , ii) Section 4, 16.1 (iv) a) | Physical test for insulation-Elongation at break (Without agenig) | Yes | Mandatory (Acceptance) | Elongation, Min, (Unit : %) | Whole Number |  |  | IS 10810 Part 7 | [330 empty] | 200
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 5 , 16.1, and 16.2, Table 1 , ii) b) Section 4, 16.1 (iv) b) | Physical test for insulation-Tensile Strength variation (After agenig) | Yes | Mandatory | Tensile Strength variation, (Unit : %) | Integer |  |  | IS 10810 Part 11 | [330 empty] | -25 | 25
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 5 , 16.1, and 16.2, Table 1 , ii) c) Section 4, 16.1 (iv) b) | Physical test for insulation-Elongation variation (After ageing) | Yes | Mandatory | Elongation variation, (Unit : %) | Integer |  |  | IS 10810 Part 11 | [330 empty] | -25 | 25
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 5 , 16.1, and 16.2, Table 1 , iii) a) Section 4, 16.1 (iv) c) | Physical test for insulation-Hot Set Elongation | Yes | Mandatory | Hot set Elongation, Max.(Unit : %) | Whole Number |  |  | IS 10810 Part 30 | [331 empty] | 175
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 5 , 16.1, and 16.2, Table 1 , iii) a) Section 4, 16.1 (iv) d) | Physical test for insulation-Permanent Set Elongation | Yes | Mandatory | Permanent set Elongation, Max,(Unit : %) | Whole Number |  |  | IS 10810 Part 30 | [331 empty] | 15
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 5 , 16.1, and 16.2, Table 1 , iii) a) | Physical test for insulation-Shrinkage test | Yes | Mandatory | Shrinkage, Max, (Unit : %) | Whole Number |  |  | IS 10810 Part 12 | [331 empty] | 4
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 5 , 16.1, and 16.2, Table 1 , iii) a) | Physical test for insulation-Water absorption (Gravimetric) | Yes | Mandatory | Water absorption, Max, (Unit : mg/cm2) | Whole Number |  |  | IS 10810 Part 33 | [331 empty] | 1
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8.4, 6.3, 8.3 , 16.1, and 16.4, IS 5831 | Physical test for outer sheath-Tensile Strength at break (Without agenig) | Yes | Mandatory (Acceptance) | Tensile Strength, Min, (Unit : N/mm2) | (Value upto 1 decimal places) | Type of outer sheath |  | IS 10810 Part 7 | [276 empty] | 12.5 |  | 12.5 |  | 9 |  | 12.5
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8.4 , 6.3, 8.3, 16.1, and 16.4, IS 5831 | Physical test for outer sheath-Elongation at break (Without agenig) | Yes | Mandatory (Acceptance) | Elongation, Min, (Unit : %) | Whole Number | Type of outer sheath |  | IS 10810 Part 7 | [276 empty] | 150 |  | 300 |  | 125 |  | 300
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8.4 , 6.3, 8.3, 16.1, and 16.4, IS 5831 | Physical test for outer sheath-Tensile Strength at break (After agenig) | Yes | Mandatory (Acceptance) | Tensile Strength, Min, (Unit : N/mm2) | (Value upto 1 decimal places) | Type of outer sheath |  | IS 10810 Part 11 | [276 empty] | 12.5 |  |  |  | 9 |  | 10
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8.4 , 6.3, 8.3, 16.1, and 16.4, IS 5831 | Physical test for outer sheath-Elongation at break (After agenig) | Yes | Mandatory (Acceptance) | Elongation, Min, (Unit : %) | Whole Number | Type of outer sheath |  | IS 10810 Part 11 | [276 empty] | 150 |  | 300 |  | 100 |  | 300
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8.4 , 6.3, 8.3, 16.1, and 16.4, IS 5831 | Physical test for outer sheath-Tensile Strength at break %Variation | Yes | Mandatory (Acceptance) | Tensile Strength Variation Max, (Unit : %) | Integers | Type of outer sheath |  | IS 10810 Part 11 | [277 empty] | ±25 |  |  |  | ±40 |  | ±30
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8.4 , 6.3, 8.3, 16.1, and 16.4, IS 5831 | Physical test for outer sheath-Elongation at break (After agenig) | Yes | Mandatory (Acceptance) | Elongation variation, Max, (Unit : %) | Integers | Type of outer sheath |  | IS 10810 Part 11 | [277 empty] | ±25 |  |  |  | ±40
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8.4 , 6.3, 8.3, 16.1, and 16.4, IS 5831 | Physical test for outer sheath-Hot deformation | Yes | Mandatory (Acceptance) | Hot deformation, Max, (Unit : %) | Whole Number | Type of outer sheath |  | IS 10810 Part 15 | [277 empty] | 50 |  | 50 |  | 50 |  | 50
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8.4 , 6.3, 8.3, 16.1, and 16.4, IS 5831 | Physical test for outer sheath-Shrinkage | Yes | Mandatory (Acceptance) | Shrinkage, Max, (Unit : %) | Whole Number | Type of outer sheath |  | IS 10810 Part 12 | [277 empty] | 4 | [5 empty] | 3
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8.4 , 6.3, 16.1, and 16.4, IS 5831 Table 1B | Physical test for outer sheath-Water absorption (Gravimetric) | Yes | Mandatory | Water absorption, Max, (Unit :mg/cm2) | Whole Number | Type of outer sheath |  | IS 10810 Part 33 | [277 empty] | 1 |  |  | 10
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8, 15 , IS 5831 , Section 4 | Physical test for outer sheath-Loss of Mass in air oven | Yes | Mandatory | Loss of mass, Max, (Unit :mg/cm2) | Whole Number | Type of outer sheath |  | IS 10810 Part 10 | [277 empty] | 2
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8, 15 , IS 5831 , Section 4 | Physical test for outer sheath-Thermal Stability | Yes | Mandatory | Thermal stability, Min, (Unit : minutes) | Whole Number | Type of outer sheath |  | IS 10810 Part 60 | [276 empty] | 80
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Clause 8, 15 , IS 5831 , Section 4 | Physical test for outer sheath-Heat Shock | Yes | Mandatory | Heat Shock | Satisfactory/ Unsatisfactory (Cracks) | Type of outer sheath |  | IS 10810 Part 14
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8, 15 , Table 1A Section 4, | Physical test for outer sheath-Carbon black content (For black sheath only) | Yes | Mandatory | Carbon black content (PE Sheath only), (Unit : %) | (Value upto 1 decimal places) | Type of outer sheath |  | IS 10810 Part 32 | [330 empty] | 2 | 3
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8, 15 , 17.10, Table 1B Section 4, As per annex F of 17505 Part 0 | Physical test for outer sheath- pH & Conductivity | Yes | Mandatory | pH, Min | (Value upto 1 decimal places) | Type of outer sheath | Annex F | IS 17505 part 1 | [280 empty] | 4.3 |  | 4.3 | [47 empty] | 4.3
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8, 15 , 17.10, Table 1B Section 4, As per annex F of 17505 Part 1 | Physical test for outer sheath- pH & Conductivity | Yes | Mandatory | Conductivity, Max, (Unit :uS/mm) | Whole Number | Type of outer sheath | Annex F | IS 17505 part 1 | [281 empty] | 10 |  | 10 | [47 empty] | 10
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8, 15 , 17.10, Table 1B Section 4, As per annex F of 17505 Part 1 | Physical test for outer sheath- 'HCI | Yes | Mandatory | HCl, Max, (Unit : %) | (Value upto 1 decimal places) | Type of outer sheath | Annex F | IS 17505 part 1 | [281 empty] | 0.5% |  | 0.5% | [47 empty] | 0.5
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Clause 8, 15 , IS 5831 , Section 4, Table 1B | Physical test for outer sheath-Cold bend test | Yes | Mandatory | Cold bend test | Satisfactory/Unsatisfactory (Cracks observed) |  |  | IS 10810 Part 20
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Clause 8, 15 , IS 5831 , Section 4, Table 1B | Physical test for outer sheath-Cold Elongation | Yes | Mandatory | Cold Elongation, Max, (unit: %) | Whole Number |  |  | IS 10810 Part 21 | [281 empty] | 20% |  | 20%
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Clause 8, 15 , IS 5831 , Section 4, Table 1B | Physical test for outer sheath-Cold Impact test | Yes | Mandatory | Cold Impact test | Satisfactory/Unsatisfactory (Cracks observed) |  |  | IS 10810 Part 21
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Table 1 (vi) | Insulation Resistance Test (Volume Resistivity - Room temp) | Yes | Mandatory (Acceptance) | Volume Resistivity - Room temp, ohm-cm, Min. | Whole Number |  |  | IS 10810 Part 43 | [330 empty] | 1 x 10^14
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Table 1 (vi) | Insulation Resistance Test (Volume Resistivity - Maximum temp) | Yes | Mandatory | Volume Resistivity - Maximum temp, ohm-cm, Min. | Whole Number |  |  | IS 10810 Part 43 | [330 empty] | 1 x 10^12
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Table 1 (vii), Clause 17.2 | AC High Voltage Test (Water Immersion) | Yes | Mandatory | The cables shall withstand a voltage of 3 kV a.c. (rms) at a frequency of 40 Hz to 60 Hz or dc voltage of 7.2 kV, between conductors and between conductors and ECC (if any) for a period of 5 min for each test connection | Satisfactory/Unsatisfactory (Not withstood) |  |  | IS 10810 Part 45
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Table 1 (viii), Clause 17.3 | Flammability Test | Yes | Mandatory | Period of burning after flame removal, Sec, Max. | Whole Number |  |  | IS 10810 Part 53 | [331 empty] | 60
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Table 1 (ix) a) 1) b) 1) c) 1) Clause 17.4 | Oxygen Index Test | Yes | Mandatory | Oxygen index, Max, (Unit : %) | Whole Number | Category of cable |  | IS 10810 Part 58 | [331 empty] | 29
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Table 1 (ix) a) 2) b) 2 c) 2 Clause 17.9 | Temperature Index Test | Yes | Mandatory | Minimum measured value of temperature index, Min, (Unit : °C.) | Whole Number | Category of cable |  | IS 10810 Part 64 | [330 empty] | 250
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Qualitative | Table 1 (ix) a) 3) b) 3, c)3 Clause 17.5 | Flame Retardance Test on Single cable | Yes | Mandatory | After the test, there should be no visible damages on the test specimen within 300 mm from its upper end | Satisfactory/ Unsatisfactory (Cracks) | Category of cable |  | IS 10810 Part 61
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Table 1 (ix) a) 4) b) 4, c)4 Clause 17.6 | Flame Retardance Test on Bunched cable | Yes | Mandatory | After burning has ceased, the cables should be wiped clean and the charred or affected portion should not have reached a height exceeding 2.5 m above the bottom edge of the burner, measured at the front and rear of the cable assembly (Unit : m), Max | (Value upto 1 decimal places) | Category of cable |  | IS 10810 Part 61 | [331 empty] | 2.5
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Table 1 (ix) b) 5, c)5 Clause 17.8 | Smoke Density Test | Yes | Mandatory | Smoke density, Max, (Unit :%) | Whole Number | Category of cable |  | IS 13360 Part 6 Section 9 | [331 empty] | 60
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Table 1 (ix) b) 6, c)6 Clause 17.7 | Test for Halogen Acid Gas Evolution | Yes | Mandatory | The level of halogen acid gas , Max, (Unit: %) | Whole Number | Category of cable |  | IS 10810 Part 59 | [331 empty] | 20
7098 | 1 | 0 | 2025 | 0 | Crosslinked Polyethylene Insulated Thermoplastic Sheathed Cables — Specification Part 1 For Working Voltages up to and including 1100 Volt | Electrical | Quantitative | Table 1 (ix) , c)7 Clause 17.11 | Test for Light Transmission | Yes | Mandatory | Light transmittance, (Min).(unit: %) | Whole Number | Category of cable |  | IS 10810 Part 63 | [330 empty] | 70

## Sheet2
Conductor material | No of Cores | Type of armour | Size of armour | compound of outer sheath | Type of outer sheath | Conductor grade | Size of cable | Class of conductor | Type of Insulation | Type of Tests | category of cable | Declared Value 5 [any other declaration] | Declared Value 6 [any other declaration] | "[DATA]" is any other information of the product needed for carrying out some tests. This information can be qualitative or quantitative
Copper | Single core |  |  | PVC | ST 2 | 0 |  | Class 1 | XLPE | Routine Test | C1
Aluminium | Multi core (Circular / Flat) |  |  | PE | ST 8 | H2 |  | Class 2 |  | Type Test | C2
|  |  |  | LSHF | ST 12 | H4 |  | Class 5 |  | Acceptance Test | C3
Optional Test
Earthed System
Unearthed System