## 7098-2
IS No. | Part | Section | Year | No. of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause/ Table/ Annex Reference | Test Parameter Name | To be tested and/or reported by Lab (Yes/No) | Mandatory or Optional | Requirement (as per Indian Standard) | Test Result/ Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference | Sample Quantity | Equipment | Remarks | Min | Max | voltage Grade 1.9/3.3 KV, Cable size 25 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 25 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 35 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 35 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 50 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 50 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 70 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 70 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 95 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 95 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 120 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 120 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 150 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 150 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 185 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 185 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 240 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 240 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 300 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 300 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 400 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 400 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 500 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 500 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 630 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 630 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 800 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 800 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 1000 mm2, single core armoured cable, Min | voltage Grade 1.9/3.3 KV, Cable size 1000 mm2, single core armoured cable, Max | voltage Grade 1.9/3.3 KV, Cable size 25 mm2, single core unarmoured & 3 core cable, Min | voltage Grade 1.9/3.3 KV, Cable size 25 mm2, single core unarmoured & 3 core cable, Max | voltage Grade 1.9/3.3 KV, Cable size 35 mm2, single core unarmoured & 3 core cable, Min | voltage Grade 1.9/3.3 KV, Cable size 35 mm2, single core unarmoured & 3 core cable, Max | voltage Grade 1.9/3.3 KV, Cable size 50 mm2, single core unarmoured & 3 core cable, Min | voltage Grade 1.9/3.3 KV, Cable size 50 mm2, single core unarmoured & 3 core cable, Max | voltage Grade 1.9/3.3 KV, Cable size 70 mm2, single core unarmoured & 3 core cable, Min | voltage Grade 1.9/3.3 KV, Cable size 70 mm2, single core unarmoured & 3 core cable, Max | voltage Grade 3.3/3.3 KV, Cable size 95 mm2, single core unarmoured & 3 core cable, Min | voltage Grade 3.3/3.3 KV, Cable size 95 mm2, single core unarmoured & 3 core cable, Max | voltage Grade 1.9/3.3 KV, Cable size 120 mm2, single core unarmoured & 3 core cable, Min | voltage Grade 1.9/3.3 KV, Cable size 120 mm2, single core unarmoured & 3 core cable, Max | voltage Grade 1.9/3.3 KV, Cable size 150 mm2, single core unarmoured & 3 core cable, Min | voltage Grade 1.9/3.3 KV, Cable size 150 mm2, single core unarmoured & 3 core cable, Max | voltage Grade 1.9/3.3 KV, Cable size 185 mm2, single core unarmoured & 3 core cable, Min | voltage Grade 1.9/3.3 KV, Cable size 185 mm2, single core unarmoured & 3 core cable, Max | voltage Grade 1.9/3.3 KV, Cable size 240 mm2, single core unarmoured & 3 core cable, Min | voltage Grade 1.9/3.3 KV, Cable size 240 mm2, single core unarmoured & 3 core cable Max | voltage Grade 1.9/3.3 KV, Cable size 300 mm2, single core unarmoured & 3 core cable Min | voltage Grade 1.9/3.3 KV, Cable size 300 mm2, single core unarmoured & 3 core cable Max | voltage Grade 1.9/3.3 KV, Cable size 400 mm2, single core unarmoured & 3 core cable Min | voltage Grade 1.9/3.3 KV, Cable size 400 mm2, single core unarmoured & 3 core cable Max | voltage Grade 1.9/3.3 KV, Cable size 500 mm2, single core unarmoured & 3 core cable Min | voltage Grade 1.9/3.3 KV, Cable size 500 mm2, single core unarmoured & 3 core cable Max | voltage Grade 1.9/3.3 KV, Cable size 630 mm2, single core unarmoured & 3 core cable Min | voltage Grade 1.9/3.3 KV, Cable size 630 mm2, single core unarmoured & 3 core cable Max | voltage Grade 1.9/3.3 KV, Cable size 800 mm2, single core unarmoured & 3 core cable Min | voltage Grade 1.9/3.3 KV, Cable size 800 mm2, single core unarmoured & 3 core cable Max | voltage Grade 1.9/3.3 KV, Cable size 1000 mm2, single core unarmoured & 3 core cable Min | voltage Grade 1.9/3.3 KV, Cable size 1000 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 25 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 25 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 35 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 35 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 50 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 50 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 70 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 70 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 95 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 95 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 120 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 120 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 150 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 150 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 185 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 185 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 240 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 240 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 300 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 300 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 400 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 400 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 500 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 500 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 630 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 630 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 800 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 800 mm2, single core armoured cable Max | voltage Grade 3.3/3.3 KV, Cable size 1000 mm2, single core armoured cable Min | voltage Grade 3.3/3.3 KV, Cable size 1000 mm2, single core armoured cable | voltage Grade 3.3/3.3 KV, Cable size 25 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 25 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 35 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 35 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 50 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 50 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 70 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 70 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 95 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 95 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 120 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 120 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 150 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 150 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 185 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 185 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 240 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 240 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 300 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 300 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 400 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 400 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 500 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 500 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 630 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 630 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 800 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 800 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.3/3.3 KV, Cable size 1000 mm2, single core unarmoured & 3 core cable Min | voltage Grade 3.3/3.3 KV, Cable size 1000 mm2, single core unarmoured & 3 core cable Max | voltage Grade 3.8/6.6 KV, Cable size 25 mm2 | voltage Grade 3.8/6.6 KV, Cable size 35 mm2 | voltage Grade 3.8/6.6 KV, Cable size 50 mm2 | voltage Grade 3.8/6.6 KV, Cable size 70 mm2 | voltage Grade 3.8/6.6 KV, Cable size 95 mm2 | voltage Grade 3.8/6.6 KV, Cable size 120 mm2 | voltage Grade 3.8/6.6 KV, Cable size 150 mm2 | voltage Grade 3.8/6.6 KV, Cable size 185 mm2 | voltage Grade 3.8/6.6 KV, Cable size 240 mm2 | voltage Grade 3.8/6.6 KV, Cable size 300 mm2 | voltage Grade 3.8/6.6 KV, Cable size 400 mm2 | voltage Grade 3.8/6.6 KV, Cable size 500 mm2 | voltage Grade 3.8/6.6 KV, Cable size 630 mm2 | voltage Grade 3.8/6.6 KV, Cable size 800 mm2 | voltage Grade 3.8/6.6 KV, Cable size 1000 mm2 | voltage Grade 6.35/11 KV, Cable size 25 mm2 | voltage Grade 6.35/11 KV, Cable size 35 mm2 | voltage Grade 6.35/11 KV, Cable size 50 mm2 | voltage Grade 6.35/11 KV, Cable size 70 mm2 | voltage Grade 6.35/11 KV, Cable size 95 mm2 | voltage Grade 6.35/11 KV, Cable size 120 mm2 | voltage Grade 6.35/11 KV, Cable size 150 mm2 | voltage Grade 6.35/11 KV, Cable size 185 mm2 | voltage Grade 6.35/11 KV, Cable size 240 mm2 | voltage Grade 6.35/11 KV, Cable size 300 mm2 | voltage Grade 6.35/11 KV, Cable size 400 mm2 | voltage Grade 6.35/11 KV, Cable size 500 mm2 | voltage Grade 6.35/11 KV, Cable size 630 mm2 | voltage Grade 6.35/11 KV, Cable size 800 mm2 | voltage Grade 6.35/11 KV, Cable size 1000 mm2 | voltage Grade 11/11 KV, Cable size 25 mm2 | voltage Grade 11/11 KV, Cable size 35 mm2 | voltage Grade 11/11 KV, Cable size 50 mm2 | voltage Grade 11/11 KV, Cable size 70 mm2 | voltage Grade 11/11 KV, Cable size 95 mm2 | voltage Grade 11/11 KV, Cable size 120 mm2 | voltage Grade 11/11 KV, Cable size 150 mm2 | voltage Grade 11/11 KV, Cable size 185 mm2 | voltage Grade 11/11 KV, Cable size 240 mm2 | voltage Grade 11/11 KV, Cable size 300 mm2 | voltage Grade 11/11 KV, Cable size 400 mm2 | voltage Grade 11/11 KV, Cable size 500 mm2 | voltage Grade 11/11 KV, Cable size 630 mm2 | voltage Grade 11/11 KV, Cable size 800 mm2 | voltage Grade 11/11 KV, Cable size 1000 mm2 | voltage Grade 12.7/22 KV, Cable size 25 mm2 | voltage Grade 12.7/22 KV, Cable size 35 mm2 | voltage Grade 12.7/22 KV, Cable size 50 mm2 | voltage Grade 12.7/22 KV, Cable size 70 mm2 | voltage Grade 12.7/22 KV, Cable size 95 mm2 | voltage Grade 12.7/22 KV, Cable size 120 mm2 | voltage Grade 12.7/22 KV, Cable size 150 mm2 | voltage Grade 12.7/22 KV, Cable size 185 mm2 | voltage Grade 12.7/22 KV, Cable size 240 mm2 | voltage Grade 12.7/22 KV, Cable size 300 mm2 | voltage Grade 12.7/22 KV, Cable size 400 mm2 | voltage Grade 12.7/22 KV, Cable size 500 mm2 | voltage Grade 12.7/22 KV, Cable size 630 mm2 | voltage Grade 12.7/22 KV, Cable size 800 mm2 | voltage Grade 12.7/22 KV, Cable size 1000 mm2 | voltage Grade 19/33 KV, Cable size 25 mm2 | voltage Grade 19/33 KV, Cable size 35 mm2 | voltage Grade 19/33 KV, Cable size 50 mm2 | voltage Grade 19/33 KV, Cable size 70 mm2 | voltage Grade 19/33 KV, Cable size 95 mm2 | voltage Grade 19/33 KV, Cable size 120 mm2 | voltage Grade 19/33 KV, Cable size 150 mm2 | voltage Grade 19/33 KV, Cable size 185 mm2 | voltage Grade 19/33 KV, Cable size 240 mm2 | voltage Grade 19/33 KV, Cable size 300 mm2 | voltage Grade 19/33 KV, Cable size 400 mm2 | voltage Grade 19/33 KV, Cable size 500 mm2 | voltage Grade 19/33 KV, Cable size 630 mm2 | voltage Grade 19/33 KV, Cable size 800 mm2 | voltage Grade 19/33 KV, Cable size 1000 mm2 | voltage Grade 33/33 KV, Cable size 25 mm2 | voltage Grade 33/33 KV, Cable size 35 mm2 | voltage Grade 33/33 KV, Cable size 50 mm2 | voltage Grade 33/33 KV, Cable size 70 mm2 | voltage Grade 33/33 KV, Cable size 95 mm2 | voltage Grade 33/33 KV, Cable size 120 mm2 | voltage Grade 33/33 KV, Cable size 150 mm2 | voltage Grade 33/33 KV, Cable size 185 mm2 | voltage Grade 33/33 KV, Cable size 240 mm2 | voltage Grade 33/33 KV, Cable size 300 mm2 | voltage Grade 33/33 KV, Cable size 400 mm2 | voltage Grade 33/33 KV, Cable size 500 mm2 | voltage Grade 33/33 KV, Cable size 630 mm2 | voltage Grade 33/33 KV, Cable size 800 mm2 | voltage Grade 33/33 KV, Cable size 1000 mm2 | Calculated Diameter Under Armour, For all diameter in excess of 13 mm, Min | Calculated Diameter Under Armour, For all diameter in excess of 13 mm, Max | Calculated Diameter, upto 13 mm, Min | Calculated Diameter, upto 13 mm, Max | Calculated Diameter, Over 13 mm including upto 25 mm, Min | Calculated Diameter, Over 13 mm including upto 25 mm, Max | Calculated Diameter, Over 25 mm including upto 40 mm, Min | Calculated Diameter, Over 25 mm including upto 40 mm, Max | Calculated Diameter, Over 40 mm including upto 55 mm, Min | Calculated Diameter, Over 40 mm including upto 55 mm, Max | Calculated Diameter, Over 55 mm including upto 70 mm, Min | Calculated Diameter, Over 55 mm including upto 70 mm, Max | Calculated Diameter, Over 70 mm, Min | Calculated Diameter, Over 70 mm, Max | Calculated Diameter Over Laid Up Cores, Ref to IS 10462 (Part 1), Up to and Including 25 mm, Min | Calculated Diameter Over Laid Up Cores, Ref to IS 10462 (Part 1), Up to and Including 25 mm, Max | Calculated Diameter Over Laid Up Cores, Ref to IS 10462 (Part 1), Over 25 mm Up to and Including 35 mm, Min | Calculated Diameter Over Laid Up Cores, Ref to IS 10462 (Part 1), Over 25 mm Up to and Including 35 mm, Max | Calculated Diameter Over Laid Up Cores, Ref to IS 10462 (Part 1), Over 35 mm Up to and Including 45 mm, Min | Calculated Diameter Over Laid Up Cores, Ref to IS 10462 (Part 1), Over 35 mm Up to and Including 45 mm, Max | Calculated Diameter Over Laid Up Cores, Ref to IS 10462 (Part 1), Over 45 mm Up to and Including 55 mm, Min | Calculated Diameter Over Laid Up Cores, Ref to IS 10462 (Part 1), Over 45 mm Up to and Including 55 mm, Max | Calculated Diameter Over Laid Up Cores, Ref to IS 10462 (Part 1), Over 55 mm, Min | Calculated Diameter Over Laid Up Cores, Ref to IS 10462 (Part 1), Over 55 mm, Max | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Up to and Including 15 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 15 mm Up to and Including 25 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 25 mm Up to and Including 35 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 35 mm Up to and Including 40 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 40 mm Up to and Including 45 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 45 mm Up to and Including 50 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 50 mm Up to and Including 55 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 55 mm Up to and Including 60 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 60 mm Up to and Including 65 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 65 mm Up to and Including 70 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 70 mm Up to and Including 75 mm, min | Calculated Diameter Under the Outer Sheath [IS 1S462 (Part 1)],Over 75 mm, min | Nominal Wire Dimeter, 0.30 mm, Min | Nominal Wire Dimeter, 0.45 mm, Min | Nominal Wire Dimeter, 0.70 mm, Min | Nominal Wire Dimeter, 0.90 mm, Min | Nominal Wire Dimeter, 1.25 mm, Min | Nominal Wire Dimeter, 1.40 mm, Min | Nominal Wire Dimeter, 1.60 mm, Min | Nominal Wire Dimeter, 2.00 mm, Min | Nominal Wire Dimeter, 2.50 mm, Min | Nominal Wire Dimeter, 3.15 mm, Min | Nominal Wire Dimeter, 4.00 mm, Min | Formed Wire, Type 1, min | Formed Wire, Type 2, min | Wire Diameter, Up to and Including 0.21 mm, Min | Wire Diameter,over 0.21 Up to and Including 0.41 mm, Min | Wire Diameter,over 0.41 Up to and Including 1.36 mm, Min | Wire Diameter,over 1.36 mm, Min | Grade 0, Min | Grade 0, Max | Grade H2, Min | Grade H2, Max | Grade H4, Min | Grade H4, Max | Cable size 25 mm2, Min | Cable size 25 mm2, Max | Cable size 35 mm2, Min | Cable size 35 mm2, Max | Cable size 50 mm2, | Cable size 70 mm2, | Cable size 95 mm2, | Cable size 120 mm2, | Cable size 150 mm2, | Cable size 185 mm2, | Cable size 240 mm2, | Cable size 300 mm2, | Cable size 400 mm2, | Cable size 500 mm2, | Cable size 630 mm2, | Cable size 800 mm2, | Cable size 1000 mm2,
THIS ROW TO BE LEFT BLANK | [308 empty] | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | sqmm | V | V | V | V | V | V | V | V | V | mm | mm | mm | mm | mm | mm | mm | mm | mm
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 4.1 | CONDUCTOR | Yes | Mandatory | The conductors shall be composed of plain copper or aluminium wires complying with IS 8130. | To be checked based on declaration basis | Conductor Material |  | IS 8130 |  | NOT TO BE FILLED
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 4.1.1 | CONDUCTOR | Yes | Mandatory | Mining cables to be used in gassy mines shall be of copper conductor only. | To be checked based on declaration basis | Conductor Material |  | IS 8130
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 6 | SCREENING | Yes | Mandatory | The screening shall consist of one or more of the following, as specified:a) Non-metallic semi-conducting tape, b) Non-metallic semi-conducting compound, and c) Non-magnetic metallic tape wire, strip or sheath. | Satisfactory/Unsatisfactory | SCREENING MATERIAL |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 6.1.1, 19.1 v) a) | SCREENING | Yes | Mandatory | The material shall be bonded or strippable type conforming to the requirements given in Table 2. Unless otherwise specified it shall be bonded type. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 6.1.1, Table 2 i), 19.1 v) a) | Strippability test for strippable semiconducting insulation screen | Yes | Mandatory | Force required to remove semiconducting screen from insulation without damaging shall be not less than 4 N or greater than 45 N before and after ageing (Unit : N), Min | Whole Number |  | Annex B | IS 7098-2 |  |  |  |  | 4 | 45
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 6.1.1, Table 2 i), 19.1 v) a) | Resistivity test for semiconducting screen: a) Conductor screen | Yes | Mandatory | Resistivity test for semiconducting screen, Max (Unit : Ωm) | Whole Number |  | Annex E | IS 7098-2 | [5 empty] | 1000
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 6.1.1, Table 2 i), 19.1 v) a) | b) Core screen | Yes | Mandatory | Resistivity test for semiconducting screen, Max (Unit : Ωm) | Whole Number |  | Annex E | IS 7098-2 | [5 empty] | 500
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 6.1.2 | Non-magnetic Metallic Tape for Single Core Unscreened and Unarmoured Cables | Yes | Mandatory | Requirements for this tape shall be as agreed to between the purchaser and the manufacturer | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 7 | FILLERS AND INNER SHEATH | Yes | Mandatory | The fillers and inner sheath shall be of the following: a) Vulcanized or unvulcanized rubber; and b) Thermoplastic materials | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 8.1 | ARMOURING | Yes | Mandatory | Armouring shall be of the following: a) Galvanized round steel wire, and b) Galvanized formed wires, or c) Any metallic non-magnetic wire/strip. | Satisfactory/Unsatisfactory | Type of Armouring |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 8.2 | ARMOURING | Yes | Mandatory | The galvanized steel wires/strip shall comply with the requirements of IS 3975. The requirements of nonmagnetic material shall be as agreed to between the purchaser and the supplier. | Satisfactory/Unsatisfactory |  |  | IS 3975
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 9 | OUTER SHEATH | Yes | Mandatory | The outer sheath shall be of polyvinyl chloride (PVC) or polyethylene conforming to the requirements of Type ST 2 of IS 5831 or Table 3 respectively. | Satisfactory/Unsatisfactory | OUTER SHEATH MATERIAL |  | IS 5831
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 10.1 | CONDUCTOR | Yes | Mandatory | The conductor shall be of stranded construction, size 25 mm2 and above complying with Class 2 of IS 8130. | Satisfactory/Unsatisfactory |  |  | IS 8130 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 10.2 | CONDUCTOR | Yes | Mandatory | In case of 1.9/3.3 kV and 3.3/3.3 kV cables, a protective barrier may be applied between the conductor and insulation at the discretion of the manufacturer. Such barrier, when used, shall be compatible with insulating material and suitable for the operating temperature of the cable | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 11 | CONDUCTOR SCREENING | Yes | Mandatory | All cables rated above 3.3/3.3 kV shall be provided with conductor screening. Conductor screening shall be provided over the conductor by extrusion of semiconducting compound or a combination of nonmetallic semi conducting tape and extrusion of semi conducting compound. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 12.1 | INSULATION | Yes | Mandatory | The conductor (with protective barrier or screen, where applied) shall be provided with cross linked polyethylene insulation applied by extrusion. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 12.4 | Eccentricity and Ovality | Yes | Mandatory | Eccentricity of insulation shall not exceed 15 percent when tested as per Annex A. (Unit : %), Max | Whole Number |  | Annex A | IS 7098-2 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable |  | 15
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 12.5 | Application of Insulation | Yes | Mandatory | The insulation shall be so applied that it fits closely on the conductor (or conductor screening or barrier if any) and it shall be possible to remove it without damaging the conductor | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 13.1 | INSULATION SCREENING | Yes | Mandatory | All cables rated above 3.3/3.3 kV shall be provided with insulation screening | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 13.2 | INSULATION SCREENING | Yes | Mandatory | The insulation screening shall consist of two parts; namely, metallic and non-metallic. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 13.3 | INSULATION SCREENING | Yes | Mandatory | Non-metallic part shall be applied directly over the insulation of each core and shall consist of either extruded semi-conducting compound or a combination of semi-conducting tape and extruded semi-conducting compound. The test method for strippability test for strippable semi-conducting insulation screen is given in Annex B. Semiconducting water swell-able tapes if used shall be as agreed between the purchaser and the supplier. | Satisfactory/Unsatisfactory |  | Annex B | IS 7098-2 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 13.4 | INSULATION SCREENING | Yes | Mandatory | Metallic part shall consist of either tape, or braid, or concentric serving of wires or a combination of wires and tapes or a sheath shall be non-magnetic and shall be applied over the non-metallic part. For single-core armoured cables, the armouring may constitute the metallic part of the screening. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 14.1 | CORE IDENTIFICATION | Yes | Mandatory | Core identification for three core cables shall be follow as for : Voltage Grade1.9/3/3 and 3.3/3.3 kV Method of Identification as a) Different colouring of XLPE insulation, or b) Coloured strips applied on the cores, or c) By numerals (1, 2, 3,) either by applying numbered strips or by printing on the cores. | Satisfactory/Unsatisfactory | Voltage grade kV |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 14.1 | CORE IDENTIFICATION | Yes | Mandatory | Core identification for three core cables shall be follow as for : Voltage Grade3.8/6.6, 6.35/11, 11/11, 12.7/22 and 19/33 kV Method of Identification as a) Coloured strips applied on the cores, or b) By numerals (1, 2, 3…) either by applying numbered strips or by printing on the cores | Satisfactory/Unsatisfactory | Voltage grade kV |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 14.1.1 | CORE IDENTIFICATION | Yes | Mandatory | For identification by using coloured strips, red, yellow and blue colours respectively shall be used to identify phase conductors. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 15.1 | LAYING UP OF CORE | Yes | Mandatory | In three core cables, the cores shall be laid together with a suitable right hand lay. Where necessary the interstices shall be filled with non-hygroscopic material. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 16.1 | INNER SHEATH (COMMON COVERING) | Yes | Mandatory | The laid up cores shall be provided with inner sheath applied either by extrusion or by wrapping. It shall be ensured that the shape is as circular as possible | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 16.2 | INNER SHEATH (COMMON COVERING) | Yes | Mandatory | The inner sheath shall be so applied that it fits closely on the laid up cores and it shall be possible to remove it without damage to the insulation | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2 |  | NOT TO BE FILLED
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 16.2.1 | INNER SHEATH (COMMON COVERING) | Yes | Mandatory | In case of single core cables where there are both metallic screening and armouring there shall be extruded inner sheath between them. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 16.3.1 | Thickness of Inner Sheath | Yes | Mandatory | When one or more layers of binder tapes are applied over the laid up cores, the thickness of the tapes shall not be construed as a part of the inner sheath. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 17.1, 19.1 (ii) | ARMOURING | Yes | Mandatory | Armouring shall be applied over the insulation or protective barrier or non-metallic part of insulation screening, if any in case of single core cables or over inner sheath in case of screened and armoured single core cables and over inner sheath in case of three cores cables. | Satisfactory/Unsatisfactory | Type of armour |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 17.1.1, 19.1 (ii) | ARMOURING | Yes | Mandatory | The armour wires/formed wires shall be applied as closely as practicable | Satisfactory/Unsatisfactory | Type of armour |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 17.1.2, 19.1 (ii) | ARMOURING | Yes | Mandatory | The direction of lay of armour shall be left hand for double wires/formed wires armoured cable this requirement shall apply to the inner layer of wires/ formed wires the outer layer shall, except in special cases be applied in the reverse direction to the inner layer, and there shall be a separator of suitable nonhygroscopic material: such as plastic tape bituminized Hessian cotton tape, rubber proofed tape between the inner and outer layers of armoured wires/formed wires. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 17.1.3, 19.1 (ii) | ARMOURING | Yes | Mandatory | A binder tape may be applied over the armour. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 17.2, 19.1 (ii) | Types of Armour | Yes | Mandatory | Where the calculated diameter below armouring does not exceed 13 mm, the armour shall consist of galvanized round steel wires. The armour of cables having calculated diameter below armouring greater than 13 mm shall consist of either galvanized round steel wires or galvanized formed wires | Satisfactory/Unsatisfactory | Type of armour |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 17.2.1, 19.1 (ii) | Types of Armour | Yes | Mandatory | In case of single-core cables for ac system, the armouring shall be of non-magnetic material. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.3, 19.1 (ii) | Dimensions | Yes | Mandatory | Dimension ( A) - Nominal Width of Steel Strip as per table 6 (Unit: mm) | (Value upto 2 decimal places) | Type of armour |  | IS 3975 | 1 | [215 empty] | 3.6 | 4.4 |  |  | 3.6 | 4.4 | 3.6 | 4.4 | 5.49 | 6.71 | 5.49 | 6.71 | 5.49 | 6.71
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.3, 19.1 (ii) | Dimensions | Yes | Mandatory | Dimension (C) - Nominal Thicness of Steel Strip as per table 6 (Unit: mm) | (Value upto 2 decimal places) | Type of armour |  | IS 3975 | 2 | [215 empty] | 0.72 | 0.88 |  |  | 0.72 | 0.88 | 0.72 | 0.88 | 1.26 | 1.54 | 1.26 | 1.54 | 1.26 | 1.54
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.3, 19.1 (ii) | Dimensions | Yes | Mandatory | Dimension -Nominal Diameter of Round Wire as per table 6 (Unit: mm) | (Value upto 2 decimal places) | Type of armour |  | IS 3975 | 3 | [217 empty] | 1.36 | 1.44 | 1.555 | 1.645 | 1.95 | 2.05 | 2.435 | 2.565 | 3.07 | 3.23 | 3.9 | 4.1
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.4, 19.1 (ii) | Joints | Yes | Mandatory | The joints in armour wires or formed wires shall be made by brazing or welding and the surface irregularities shall be removed. A joint in any wires/ formed wires shall be at least 300 mm from the nearest joint in any other armoured wire/formed wires in the completed cable | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.5, 19.1 (ii) | Resistance | Yes | Mandatory | In case of cable for use in mines the resistance of armoured shall be not exceed that of conductor as specified in IS 8130 by more than 33 percent. formed wires in armour by required number of tinned copper wires/formed wires is permissible. (Unit : ohm/km) | (Value upto 3 decimal places) |  |  | IS 8130
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.6.1, 19.1 (ii) | ARMOURING | Yes | Mandatory | The tensile strength of round steel wire/formed steel wire , (Unit: N/mm2) | Whole Number |  |  | IS 10810-37 |  |  |  |  | 250 | 580
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.6.2, 19.1 (ii) | ARMOURING | Yes | Mandatory | The elongation at break of round steel wire/formed steel wire, (Unit: %) | Whole Number |  |  | IS 10810-37 |  |  |  |  | 6
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.6.3, 19.1 (ii) | ARMOURING | Yes | Mandatory | Round steel wire shall meet the requirements of torsion test. The gauge length between vices and the minimum number of turns without break shall be as per Table 6 of IS 3975. | Whole Number |  |  | IS 10810-38 | [218 empty] | 43 |  | 37 |  | 30 |  | 24 |  | 19 |  | 15
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 17.6.4, 19.1 (ii) | ARMOURING | Yes | Mandatory | The zinc coating shall not show any cracks and shall not flake off on rubbing by the bare finger when the formed steel wire is subjected to winding test. | Satisfactory/Unsatisfactory (Crack observed) |  |  | IS 10810-40
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 17.6.5, 19.1 (ii) | ARMOURING | Yes | Mandatory | The uniformity of zinc coating of round steel wire/formed steel wire shall comply with the requirements of IS 3975 subject to the following: a) The minimum number of dips shall be reduced by one half-minute dip, and b) In case of formed wires, dip test is applicable only for the face. | Satisfactory/Unsatisfactory (Crack observed) |  |  | IS 10810-40
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.6.6, 19.1 (ii) | ARMOURING | Yes | Mandatory | The mass of zinc coating of round steel wire shall not be less than 95 percent of the mass specified in Table 2 of IS 4826. (Unit : g/m2) | (Value upto 1 decimal places) |  |  | IS 10810-41 | [218 empty] | 85.5 |  | 90.25 |  | 99.75 |  | 104.5 |  | 114 |  | 128.25
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.6.6, 19.1 (ii) | ARMOURING | Yes | Mandatory | The mass of zinc coating of formed steel wire shall not be less than 95 percent of the mass specified in IS 3975.(Unit : g/m2) | (Value upto 1 decimal places) |  |  | IS 3975 | [216 empty] | 104.5 |  |  |  | 104.5 |  | 104.5 | . | 104.5 |  | 104.5 |  | 104.5 | [34 empty] | 104.5 | 171
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 17.6.7, 19.1 (ii) | ARMOURING | Yes | Mandatory | The resistivity of the round steel wire/formed steel wire, (Unit : ohm-cm), Max | (Value upto 1 decimal places X 10^6) |  |  | IS 10810-42 | [5 empty] | 14.5 X 10^6
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 18.1 | OUTER SHEATH | Yes | Mandatory | The outer sheath shall be applied by extrusion. It shall be applied: a) Over the non-magnetic metallic tape covering. The insulation or over The nonmagnetic metallic part of insulation screening in case of un-armoured single core cables, and b) Over the armouring in case of armoured cables. | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 18.2 | OUTER SHEATH | Yes | Mandatory | Colour of outer sheath shall be black or any other colour as agreed to between the purchaser and the supplie | Satisfactory/Unsatisfactory |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 i) a) | Annealing test (for copper) (Befor stranding) | Yes | Mandatory | This test shall be carried out in accordance with IS 10810 (Part 1). The elongation shall be not less than the appropriate value given in Cl7.1.2.1 in IS 8130. (Unit : %) | (Value upto 1 decimal places) |  |  | IS 10810-1 | [265 empty] | 9 | 13.5 | 18 | 22.5
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 i) b) | Tensile test (for aluminium) (Before stranding) | Yes | Mandatory | This test shall be carried out in accordance with IS 10810 (Part 2). The sample shall meet the requirements given in Cl.7.2.1 of IS 8130. (Unit : N/mm2) | (Value upto 1 decimal places) |  |  | IS 10810-2 | [269 empty] | 0 | 100 | 100 | 150 | 150
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 i) b) | Tensile test (for aluminium) (After stranding) | Yes | Mandatory | This test shall be carried out in accordance with IS 10810 (Part 2). The sample shall meet the requirements given in Cl.7.2.1 of IS 8130.(Unit : N/mm2) | (Value upto 1 decimal places) |  |  | IS 10810-2 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable | [265 empty] | 0 | 95 | 95 | 142.5 | 142.5
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 19.1 i) c) | Wrapping test (for aluminium) | Yes | Mandatory | This test shall be done in accordance with IS 10810 (Part 3). The criteria for passing is that the wire shall not break. | Satisfactory/Unsatisfactory (Break) |  |  | IS 10810-3 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 i) d) | Resistance test( Copper conductor) | Yes | Mandatory | The corrected dc resistance shall not exceed the values given in the appropriate Table 1 to Table 5 of IS 8130 | (Value upto 3 decimal places) |  |  | IS 10810-5 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable | [272 empty] | 0.727 |  | 0.524 | 0.387 | 0.268 | 0.193 | 0.153 | 0.124 | 0.0991 | 0.0754 | 0.0601 | 0.047 | 0.0366 | 0.0283 | 0.0221 | 0.0176
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 i) d) | Resistance test(Aluminimum conductor) | Yes | Mandatory | The corrected dc resistance shall not exceed the values given in the appropriate Table 1 to Table 5 of IS 8130 | (Value upto 3 decimal places) |  |  | IS 10810-5 | 2 |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable | [272 empty] | 1.2 |  | 0.868 | 0.641 | 0.443 | 0.32 | 0.253 | 0.206 | 0.164 | 0.125 | 0.1 | 0.0778 | 0.0605 | 0.0469 | 0.0367 | 0.0291
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iii) a), 5 | Tensile strength | Yes | Mandatory | Tensile strength , Min(Unit : N/mm2 | (Value upto 1 decimal places) |  |  | IS 10810-7 | 1 |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable | 12.5
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iii) a), 5 | Elongation at break | Yes | Mandatory | Elongation at break, Min (Unit : %) | Whole Number |  |  | IS 10810-7 | 2 |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable | 200
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iii) b), 5 | Ageing in air oven, Tensile strength variation | Yes | Mandatory | Ageing in air oven, Tensile strength variation, Max (Unit : %) | Integers |  |  | IS 10810-11 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable | -25 | 25
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iii) b), 5 | Ageing in air oven, Elongation variation | Yes | Mandatory | Ageing in air oven, Elongation variation, Max (Unit : %) | Integers |  |  | IS 10810-11 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable | -25 | 25
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iii) d), 5 | Hot set test, Elongation under load | Yes | Mandatory | Hot set test, Elongation under load, Max (Unit : %) | Whole Number |  |  | IS 10810-30 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable |  | 175
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iii) d), 5 | Hot set test, Permanent elongation (set) after cooling | Yes | Mandatory | Hot set test, Permanent elongation (set) after cooling, Max (Unit : %) | Whole Number |  |  | IS 10810-30 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable |  | 15
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iii) e), 5 | Shrinkage test | Yes | Mandatory | Shrinkage test, Min (Unit : %) | Whole Number |  |  | IS 10810-12 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable | 4
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iii) f), 5 | Water absorption test (gravimetric) | Yes | Mandatory | Water absorption test (gravimetric), Max(Unit : mg/cm2) | Whole Number |  |  | IS 10810-33 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable |  | 1
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iv), 12.2 | Thickness of insulation, Nominal | Yes | Mandatory | Nominal thickness compliance shall be checked by testing the dimensional requirements specified in Table 4 and as per test method given in IS 10810 (Part 6) (Unit : mm) | (Value upto 2 decimal places) | Voltage grade kV, Size of Cable |  | IS 10810-6 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable |  |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.6 |  | 2.8 |  | 3 |  | 3.3 |  | 3.5 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.4 |  | 2.6 |  | 2.8 |  | 3 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.6 |  | 2.8 |  | 3 |  | 3.3 |  | 3.5 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.4 |  | 2.6 |  | 2.8 |  | 3 |  | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 3 | 3.3 | 3.5 | 3.5 | 3.5 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 |  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iv), 12.3 | Thickness of insulation, Minimum | Yes | Mandatory | Nominal thickness compliance shall be checked by testing the dimensional requirements specified in Table 4 and as per test method given in IS 10810 (Part 6) (Unit : mm) | (Value upto 2 decimal places) | Voltage grade kV, Size of Cable |  | IS 10810-6 |  |  |  | Number of observation : 01 for Single core cable, 03 for Three core cable |  |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.24 |  | 2.42 |  | 2.6 |  | 2.87 |  | 3.05 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 2.06 |  | 2.24 |  | 2.42 |  | 2.6 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.15 |  | 2.24 |  | 2.42 |  | 2.6 |  | 2.87 |  | 3.05 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 1.88 |  | 2.06 |  | 2.24 |  | 2.42 |  | 2.6 |  | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.6 | 2.87 | 3.05 | 3.05 | 3.05 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 4.85 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iv), 16.3 | Thickness of Inner Sheath, Minimum | Yes | Mandatory | The thickness of inner sheath (common covering) shall be as given in Table 5 single core cables except those specified on 15.2.1 shall have no inner sheath. | (Value upto 2 decimal places) | Voltage grade kV, Size of Cable |  | IS 10810-6 | [230 empty] | 0.3 |  | 0.4 |  | 0.5 |  | 0.6 |  | 0.7
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iv), 18.3.1 | Thickness of Outer Sheath for Unarmoured Cables, Nominal | Yes | Mandatory | The thickness of outer sheath of unarmoured cables determined by taking the average of a number of measurements shall be not less than the nominal value specified in col 3 of Table 7 and the smallest of the measured values shall not fall below the nominal value specified in col 4 of Table 7. (Unit : mm) | (Value upto 2 decimal places) | Voltage grade kV, Size of Cable |  | IS 10810-6 | [240 empty] | 1.8 | 2 | 2.2 | 2.4 | 2.6 | 2.8 | 3 | 3.2 | 3.4 | 3.6 | 3.8 | 4
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 iv), 18.3.2 | Minimum Thickness of Outer Sheath for Armoured Cables/ un Armoured Cables | Yes | Mandatory | The thickness of outer sheath shall not be less than the minimum value specified in col 5 of Table 7. (Unit : mm) | (Value upto 2 decimal places) | Voltage grade kV, Size of Cable |  | IS 10810-6 | [240 empty] | 1.24 | 1.4 | 1.56 | 1.72 | 1.88 | 2.04 | 2.2 | 2.36 | 2.52 | 2.68 | 2.84 | 3
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 v) b) | VolumeResistivity test for semiconducting screen a) Conductor screen | Yes | Mandatory | VolumeResistivity test for semiconducting screen, 1000 Ω m, Max (Unit : Ω m) | Whole Number |  | Table 2 and Annex E | IS 7098-2 | [5 empty] | 1000
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 v) b) | VolumeResistivity test for semiconducting screen b) Core screen | Yes | Mandatory | VolumeResistivity test for semiconducting screen, 500 Ω m, Max (Unit : Ω m) | Whole Number |  | Table 2 and Annex E | IS 7098-2 | [5 empty] | 500
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) a) | Tensile strength , ST2 Sheath | Yes | Mandatory | Tensile strength, Min(Unit : N/mm2) | (Value upto 1 decimal places) |  |  | IS 10810-7 |  |  |  |  | 12.5
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) a) | Tensile strength ,PE Sheath | Yes | Mandatory | Tensile strength, Min(Unit : N/mm2) | (Value upto 1 decimal places) |  |  | IS 10810-7 |  |  |  |  | 12.5
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) a) | Elongation at break, ST2 Sheath | Yes | Mandatory | Elongation at break, Min (Unit : %) | Whole Number |  |  | IS 10810-7 |  |  |  |  | 150
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) a) | Elongation at break, PE Sheath | Yes | Mandatory | Elongation at break, Min (Unit : %) | Whole Number |  |  | IS 10810-7 |  |  |  |  | 300
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) b) | Ageing in air oven : Tensile stregth, ST2 Sheath | Yes | Mandatory | Ageing in air oven : Tensile stregth, ST2 Sheath, Min(Unit : N/mm2) | (Value upto 1 decimal places) |  |  | IS 10810-11 |  |  |  |  | 12.5
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) b) | Ageing in air oven : Tensile stregth Variation, ST2 Sheath | Yes | Mandatory | Ageing in air oven : Tensile stregth Variation, ST2 Sheath, Max (Unit : %) | Integers |  |  | IS 10810-11 |  |  |  |  | -25 | 25
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) b) | Ageing in air oven : Elongation, ST2 Sheath | Yes | Mandatory | Ageing in air oven : Elongation, ST2 Sheath, Min (Unit : %) | Whole Number |  |  | IS 10810-11 |  |  |  |  | 150
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) b) | Ageing in air oven : Elongation Variation , ST2 Sheath | Yes | Mandatory | Ageing in air oven : Elongation Variation , ST2 Sheath, Max (Unit : %) | Integers |  |  | IS 10810-11 |  |  |  |  | -25 | 25
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) b) | Ageing in air oven : Elongation, PE Sheath | Yes | Mandatory | Ageing in air oven : Elongation, PE Sheath, Min (Unit : %) | Integers |  |  | IS 10810-11 |  |  |  |  | 300
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) c) | Shrinkage test | Yes | Mandatory | Shrinkage test, Max (Unit : %) | Integers |  |  | IS 10810-12 | [5 empty] | 4
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) d) | Hot deformation, ST2 Sheath | Yes | Mandatory | Hot deformation, ST2 Sheath, Max (Unit : %) | Integers |  |  | IS 10810-15 | [5 empty] | 50
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) d) | Hot deformation, PE Sheath | Yes | Mandatory | Hot deformation, PE Sheath, Max (Unit : %) | Integers |  |  | IS 10810-15 | [5 empty] | 50
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) e) | Loss of mass in air oven | Yes | Mandatory | Loss of mass in air oven, mg/cm2, Max | Integers |  |  | IS 10810-10 | [5 empty] | 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 19.1 vi) f) | Heat shock | Yes | Mandatory | Heat shock, No sign of cracks | Satisfactory/Unsatisfactory (Crack observed) |  |  | IS 10810-14
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) g) | Thermal stability | Yes | Mandatory | Thermal stability, minutes, Min | (Integers) |  |  | IS 10810-60 | To be only filled if the Column I and Column J are having same information and Column M is having different information | NOT TO BE FILLED |  |  | 80
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vi) h) | Carbon black content of polythene sheath | Yes | Mandatory | Carbon black content of polythene sheath, (Unit : %) | Whole Number |  |  | IS 10810-32 |  |  |  |  | 2 | 3
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vii) | Thermal ageing test for complete cable | Yes | Mandatory | a) Conductor screen ,ohm. m, Max | Whole Number |  | 20.9 | IS 7098-2 | [5 empty] | 1000
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 vii) | Thermal ageing test for complete cable | Yes | Mandatory | b) Insulation screen, ohm. m, Max | Whole Number |  | 20.9 | IS 7098-2 | [5 empty] | 500
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 viii) | Partial discharge test, Routine test & Acceptance test | Yes | Mandatory | Partial discharge test, Routine test & Acceptance test, pC, Max | Whole Number |  | 20.2 | IS 7098-2 | [5 empty] | 10
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 viii) | Partial discharge test, Type test | Yes | Mandatory | Partial discharge test, Type test, pC, Max | Whole Number |  | 20.2 | IS 7098-2 | [5 empty] | 5
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 ix) | Bending test, Routine test & Acceptance test | Yes | Mandatory | Bending test, Routine test & Acceptance test, pC, Max | Whole Number |  | 20.3 | IS 7098-2 | [5 empty] | 10
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 ix) | Bending test, Type test | Yes | Mandatory | Bending test, Type test, pC, Max | Whole Number |  | 20.3 | IS 7098-2 | [5 empty] | 5
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 x) a) | Dielectric Power Factor Test. As a function of voltage | Yes | Mandatory | The measured value of tan δ at Uo shall not exceed 0.004 | (Value upto 3 decimal places) |  | 20.4 | IS 7098-2 | [5 empty] | 0.004
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 x) a) | Dielectric Power Factor Test. As a function of voltage | Yes | Mandatory | the increment of tan δ between 0.5 Uo and 2 Uo shall not be more than 0.002. | (Value upto 3 decimal places) |  | 20.4 | IS 7098-2 | [5 empty] | 0.002
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 x) b) | Dielectric Power Factor Test, As a function of temperature | Yes | Mandatory | The measured value of tanδ  shall not exceed 0.004 at ambient temperature | (Value upto 3 decimal places) |  | 20.4 | IS 7098-2 | [5 empty] | 0.004
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 x) b) | Dielectric Power Factor Test, As a function of temperature | Yes | Mandatory | The measured value of tanδ  shall not exceed 0.008 at 5 °C to 10 °C above the maximum conductor temperature in normal operation. | (Value upto 3 decimal places) |  | 20.4 | IS 7098-2 | [5 empty] | 0.008
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 xi) | Insulation resistance (volume resistivity) test, at 27 °C | Yes | Mandatory | Insulation resistance (volume resistivity) test, at 27 °C, ohm.cm, Min | (Value upto 1 decimal places × 10^14) |  |  | IS 10810-43 |  |  |  |  | 1 × 10^14
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 xi) | Insulation resistance (volume resistivity) test, at 90 °C | Yes | Mandatory | Insulation resistance (volume resistivity) test, at 90 °C, ohm.cm, Min | (Value upto 1 decimal places × 10^12) |  |  | IS 10810-43 |  |  |  |  | 1 × 10^12
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 xii) | Heat cycle test | Yes | Mandatory | The heating cycle shall be as per Cl 19.5, After twentieth cycle, the sample shall be subjected to dielectric power factor as a function of voltage (20.4.1) and partial discharge test (see 20.2). | Satisfactory/Unsatisfactory |  |  | IS 10810-49
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 19.1 xiii) | Impulse withstand test | Yes | Mandatory | No breakdown of insulation shall occur during the test. | Satisfactory/Unsatisfactory (Breakdown occurs) |  |  | IS 10810-47
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 19.1 xiii) | Impulse withstand test | Yes | Mandatory | The temperature of the conductor shall be at 5 °C to 10 °C above the maximum conductor temperature in normal operation. | Satisfactory/Unsatisfactory |  |  | IS 10810-47
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 19.1 xiv) | High voltage test, Type/Acceptance Test | Yes | Mandatory | The cable shall withstand without breakdown an ac voltage equal to 4 Uo when applied to the sample between conductor and screen/metallic tape/armour (and between conductors in case of unscreened cable). the voltage shall be gradually increased to the specified value and maintained for a period of 4 h. | Satisfactory/Unsatisfactory (Not withstood the test) |  |  | IS 10810-45
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 19.1 xiv) | High voltage test, Routine Test | Yes | Mandatory | The cables shall withstand without any failure, the test voltages given in 20.7.2, when applied for a period of five minutes for each test connection | Satisfactory/Unsatisfactory (Not withstood the test) |  |  | ,IS 10810-45
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 xv) | Flammability test for PVC sheathed cables | Yes | Mandatory | Period of burning after removal of the flame, Sec, Max | (Integers) |  |  | IS 10810-53 | [5 empty] | 60
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1 xv) | Flammability test for PVC sheathed cables | Yes | Mandatory | the unaffected (uncharred) portion from the lower edge of the top clamp, mm, Min | (Integers) |  |  | IS 10810-53 |  |  |  |  | 50
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 19.1 xvi) | Longitudinal water penetration test | Yes | Mandatory | During the period of testing no water shall emerge from the ends of the test piece | Satisfactory/Unsatisfactory (Water Emerge) |  |  | IS 7098-2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1.3 | Oxygen index | Yes | Mandatory | Oxygen index, Min (Unit : %) | Whole Number |  |  | IS 10810-58
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 19.1.3 | Flame retardance test on single cables | Yes | Mandatory | After the test, there should be no visible damages on the test specimen within 300 mm from its upper end. | Satisfactory/Unsatisfactory (Visible damages seen) |  |  | IS 10810-61
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1.3 | Flame retardance test on bunched cables | Yes | Mandatory | affected portion should not have reached a height exceeding 2.5 m above the bottom edge of the burner, m, Max | (Value upto 1 decimal places) |  |  | IS 10810-62 | [5 empty] | 2.5
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1.3 | Temperature index | Yes | Mandatory | Temperature index, Min (Unit : °C) | Whole Number |  |  | IS 10810-64 |  |  |  |  | 250
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1.3 | Test for Smoke Density | Yes | Mandatory | Test for Smoke Density , Max (Unit : %) | Whole Number |  |  | IS 13369-6-9 | [5 empty] | 60
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Quantitative | 19.1.3 | Test for halogen acid gas evolution | Yes | Mandatory | Test for halogen acid gas evolution, Max (Unit : %) | Whole Number |  |  | IS 10810-59 | [5 empty] | 20
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 19.4 | Optional Test | Yes | Optional | Cold impact test for outer sheath, No signs of cracks or scales | Satisfactory/Unsatisfactory (signs of cracks or scales observed) |  |  | IS 10810-21
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 21.1 | The manufacturer shall be identified throughout the length of cable by manufacturers name or trade-mark and the voltage grade and year of manufacture indented, printed or embossed or by means of a tape bearing this information. the indentation, printing or embossing shall be done only on the outer sheath | Yes | Mandatory | The manufacturer shall be identified throughout the length or cable by manufacturer's name or trade mark, and the voltage grade and year of manufacture indented, printed or embossed or by means of a tape bearing this information. The indentation, printing or embossing shall be done only on the outer sheath. For manufacturer's name, if none of these methods is employed or if the purchaser so desires, colour identificauon threads in accordance with a scheme to be approved by the Bureau of Indian Standards shall be employed. | Satisfactory/Unsatisfactory (Not Marked) |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 21.2.1 | In case of cables intended for use in mines, the word ‘Mining’ shall be indented, printed or embossed on the outer sheath throughout the length of the cable. | Yes | Mandatory | In case of cables intended for use in mines, the word ‘Mining’ shall be indented, printed or embossed on the outer sheath throughout the length of the cable. | Satisfactory/Unsatisfactory (Not Marked) |  |  | IS 7098 Part 2 | To be only filled if the Column I and Column J are having same information and Column M is having different information | NOT TO BE FILLED
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 21.2.2 | The special cables with improved fire performance for Category C1 and C2 shall be identified by indenting, embossing or printing the appropriate legend on the outer sheath throughout the cable length in addition to the existing marking requirements. | Yes | Mandatory | The special cables with improved fire performance for Category C1 and C2 shall be identified by indenting, embossing or printing the appropriate legend on the outer sheath throughout the cable length in addition to the existing marking requirements. | Satisfactory/Unsatisfactory (Not Marked) |  |  | IS 7098 Part 2
IS 7098 | 2 |  | 2011 | 2 | CROSSLINKED POLYETHYLENE INSULATED THERMOPLASTIC SHEATHED CABLES — SPECIFICATION PART 2 FOR WORKING VOLTAGES FROM 3.3 kV UP TO AND INCLUDING 33 Kv | Electrical | Qualitative | 21.3 | The cable code shall be used. | Yes | Mandatory | The following codes shall beused for designating the cables: Constituent Code Letter Aluminium conductor A PVC insulation Y Steel round wire armour W Nonmagnetic round wirearmour Wa Steel strip armour F Nonmagnetic strip armour Fa Double steel wire armour WW Double steel strip armour FF PVC outer sheath Y | Satisfactory/Unsatisfactory (Not Marked) |  |  | IS 7098 Part 2

## Sheet1
o Grade, Type, Variety, Class
Conductor material | No of Cores | Size and Type of armour | Type of outer sheath | Conductor grade (0/H2/H4) | Size of cable | Class of conductor | Type of Insulation | category of cable | Voltage grade
Copper | Single core | Round Wire | ST 1 | 0 |  | Class 1 | Type A | 1
Aluminium | Multi core (Circular / Flat) | Formed wire | ST 2 | H2 |  | Class 2 | Type C | C1
|  |  | ST 3 | H4 |  | Class 5 | Type D | C2