## Sheet1
Annex-C
IS Number | Part | Section | Year | Number of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause/ Table/ Annex Reference | Test Parameter Name | To be tested and/or reported by Lab (YES / NO) | Mandatory or Optional | Characteristics (as per Indian Standard) - No specified values to be mentioned here | Test Result/ Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference | Sample Quantity | Equipment | Remarks |  |  | Specified limits for Grade 2 | Specified limits for Grade 2 | Specified limits for Grade 3 | Specified limits for Grade 3 | Specified limits for Type 1 | Specified limits for Type 1 | Specified limits for Type 2 | Specified limits for Type 2 | Specified limits for Type 3 | Specified limits for Type 3 | Specified limits for Size 1 | Specified limits for Size 1 | Specified limits for Size 2 | Specified limits for Size 2 | Specified limits for Size 3 | Specified limits for Size 3 | Specified limits for XXXX 1 | Specified limits for XXXX 1 | Specified limits for XXXX 2 | Specified limits for XXXX 2 | Specified limits for XXXX 3 | Specified limits for XXXX 3 | If the test is quantitative, the Min and Max value to be written after applying the tolerance given in the standard. If only upper and lower limit is given, mention ONLY Min or ONLY Max balue and leave the other cell blank. If the test is Qualitative, both Only Min column to be filled by the qualitiative requirement, the Max column to be left blank
THIS ROW TO BE LEFT BLANK | [20 empty] | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 2.1.1 | Types and designation | Yes | Mandatory | The tapes have been classified in two types. The tapes with their designations are given below: General Purpose Type — This type is suitable for application at temperature above 0°C, and designated as F-PVC/90/0/Tp. | Satisfactory/Unsatisfactory |  |  | 7809 part 3 sec 1 | To be only filled if the Column I and Column J are having same information and Column M is having different information | NOT TO BE FILLED
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 2.1.2 | Types and designation | Yes | Mandatory | The tapes have been classified in two types. The tapes with their designations are given below: Low Temperature Application Type — This type is suitable for application at temperature not less than —18°C, and designated as F-PVC/75/18/T. | Satisfactory/Unsatisfactory |  |  | 7810 part 3 sec 1
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | General Requirement | Yes | Mandatory | Tapes may be transparent, translucent or opaque, and be supplied coloured or uncoloured. | Satisfactory/Unsatisfactory | Transparent / Translucent/ Opaque | 4.1 | 7809(Part 1) :1975
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | General Requirement | Yes | Mandatory | Where coloured tapes are required, the preferred colours for all tapes other than those having a woven fabric base are black, blue, green, red, white and yellow. | Satisfactory/Unsatisfactory |  | 4.1 | 7809(Part 1) :1975
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | General Requirement | Yes | Mandatory | Each roll shall be reasonably free from telescoping and distortion. When unrolled, the tape shall show no transfer of adhesive to the backing of the underlying turn, tearing of the base film nor fraying of the threads. | Satisfactory/Unsatisfactory |  | 5.1 | 7809(Part 1) :1975
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.1 | General | Yes | Mandatory | Core Diameter the preferred internal diameters of the cores on which the tape is rolled are 25 mm and 75 mm. (Unit : mm) | (Value upto 2 decimal places) | Core dia | 6.1 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.2 | Width | Yes | Mandatory | The width of the tape shall be 5, 10, 15, 20, 25, 40, 50 mm or greater than 50 mm by agreement between the purchaser and the supplier. (Unit : mm) | (Value upto 2 decimal places) |  | 6.2 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.2 | Width | Yes | Mandatory | The tolerance on the stated width shall be ±1.0 mm for widths up to and including 20 mm and 1.5 mm for greater widths. | (Value upto 2 decimal places) |  | 6.2 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.3 | Length | Yes | Mandatory | The length of tape on a roll shall be 10, 25, 50 m or multiples of 50 m. The actual length shall be not less than the stated length. (Unit : mm) | (Value upto 2 decimal places) |  | 6.3 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.4.1 | Thickness | Yes | Mandatory | For the general purpose type, the preferred thicknesses are 0·125, 0·18, 0·22, 0·25 and 0·5 mm. (Unit : mm) | (Value upto 3 decimal places) |  |  | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.4.2 | Thickness | Yes | Mandatory | For the low application temperature type, the preferred thicknesses are 0·18 and 0·22 mm. (Unit : mm) | (Value upto 3 decimal places) |  |  | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.4.3 | Thickness | Yes | Mandatory | When other thicknesses are required, they shall be chosen from the R10 series of preferred numbers. (Unit : mm) | (Value upto 3 decimal places) |  |  | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.4.4 | Thickness | Yes | Mandatory | The tolerance over the entire range of thicknesses shall be ±0·025 mm, unless otherwise specified. (Unit : mm) | (Value upto 3 decimal places) |  |  | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 4.1 | Tensile strength | Yes | Mandatory | When tested in accordance with 9 of IS : 7809 (Part 2)-1977† the central value of tensile strength shall be not less than 150 N/10 mm width per mm thickness. (Unit : N/10 mm) | (Value upto 2 decimal places) |  | 9 | 7809 Part 2 (1977)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 4.2 | Adhesion to Steel | Yes | Mandatory | Adhesion to Steel — When tested in accordance with 10.3.2 of IS : 7809 (Part 2)-1977†, the central values of adhesion to steel shall not be less than 1·6 N/10 mm width. (Unit : N/10 mm) | (Value upto 2 decimal places) |  | 10.3.2 | 7809 Part 2 (1977)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 4.3 | Adhesion to Backing | Yes | Mandatory | Adhesion to Backing — When tested in accordance with 10.3.3 of IS : 7809 (Part 2)-1977†, the central value for adhesion to backing shall be not less than 1·3 N/10 mm width. (Unit : N/10 mm) | (Value upto 2 decimal places) |  | 10.3.3 | 7809 Part 2 (1977)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 4.4 | Electric Strength at Room Temparature | Yes | Mandatory | Electric Strength at Room Temperature — When tested in accordance with 12 of IS : 7809 (Part 2)-1977†, the central value of electric strength shall not be less than 40 kV/mm. (Unit : kV/mm) | (Value upto 1 decimal places) |  | 12 | 7809 Part 2 (1977)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 4.5 | Electric Strength after Humidity Condition | Yes | Mandatory | Electric Strength after Humid Conditioning — When tested in accordance with 13 of IS : 7809 (Part 2)-1977*, the central value of electric strength after 24 h at 27 ± 2°C and 93 ± 2 percent relative humidity shall be not less than 35 kV/mm. (Unit : kV/mm) | (Value upto 1 decimal places) |  | 13 | 7809 Part 2 (1977)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 4.5 | Electric Strength after Humidity Condition | Yes | Mandatory | Electric Strength after Humid Conditioning — Alternatively tape can be immersed in water for 24 h at 27 ± 2°C. This test is carried out as described in 12 after storage of the specimens for 24 hours in the 7809 Part 2 (1977) atmosphere of 27 ± 2°C and 93 ± 2 percent RH, unless otherwise specified. | (Value upto 1 decimal places) |  | 13 | 7809 Part 2 (1977)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 4.6 | Flammability | Yes | Mandatory | Flammability — When tested in accordance with 6 of IS 7809 (Part 2) : 1977, the tapes shall comply with either: (a) The requirements of 6.5(a) of IS 7809 (Part 2) : 1977 in which case it shall be designated by addition of 'FR', as indicated F-PVCp/90/0/Tp/FR or (b) The requirements of 6.5 | Satisfactory/Unsatisfactory | F-PVCp/90/0/Tp/FR | 6, 6.5(a), 6.5(b) | 7809 Part 2 (1977)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 4.6 | Flammability | Yes | Mandatory | Flammability — When tested in accordance with 6 of IS 7809 (Part 2) : 1977, the tapes shall comply with either: (b) of IS 7809 (Part 2) : 1977 in which case it shall be designated as usual and with no addition of 'FR'," | Satisfactory/Unsatisfactory |  | 6, 6.5(a), 6.5(b) | 7809 Part 2 (1977)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 4.7 | Electrolytic Corrosion | Yes | Mandatory | Electrolytic Corrosion — The electrolytic corrosion shall be measured in accordance to either visual test method as specified in 2 of IS 8516 : 1977 or the wire tensile strength method as specified in 3 of IS 8516 : 1977. | Not corrosive / corrosive |  | 4 | 7809 Part 2 (1977)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 4.7 | Electrolytic Corrosion | Yes | Mandatory | Electrolytic Corrosion — The electrolytic corrosion shall be measured in accordance to the wire tensile strength method as specified in 3 of IS 8516 : 1977.The mean value of the breaking load for unexposed wire shall be in the range of 8 N to 9 N. (Unit : N) | (Value upto 1 decimal places) |  | 4 | 7809 Part 2 (1977)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 4.8 | Stability to Accelerated Ageing | Yes | Mandatory | Stability to Accelerated Ageing — When testing for behaviour under accelerated ageing conditions by the method described in Appendix A, the layer shall part clearly from the underlayer and shall be tested for conformance to 'Adhesion to Backing' as specified in 4.3 of this standard.' | Satisfactory/Unsatisfactory |  | Appendix A | 7809 Part 3 Sec 1
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 4.9 | Insulation Resistance Test | Yes | Mandatory | Insulation Resistance Test — This test is to be performed as per 4 of IS 8516 : 1977 and in conjunction with IS 2259 : 1963. The central value of insulation resistance shall be at least 10^5 MΩ/25 mm width after 24 hours exposure at 27 ± 2°C and 93 ± 2 percent relative humidity.' (Unit : MΩ/25mm) | (Value upto 1 decimal places) |  | 4 | IS 8516, IS 2259
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.1 | Minimum Storage Life | Yes | Mandatory | After the roll of tape has been stored flat on the cut edges in the original sealed packing at a temperature between 10 and 40°C and a relative humidity of 45 to 75 percent for a period of twelve months from the date of manufacture, it shall be tested and shall comply with the requirements as prescribed in this standard.' | Satisfactory/Unsatisfactory |  | 7 | 7809(Part 1) :1975
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | Marking | Yes | Mandatory | Each unit pack, and each package containing a number of unit packs, shall have the following information clearly and indelibly marked on it: a) Designation of the tape, in accordance with 3 | Satisfactory/Unsatisfactory |  | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | Marking | Yes | Mandatory | b) Appearance of the tape according to 4, for example, transparent-uncoloured, opaque-blue, etc; | Satisfactory/Unsatisfactory | black/blue/green/red /white/yellow | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.1 | Marking | Yes | Mandatory | c) Width of the tape; | Satisfactory/Unsatisfactory | Nominal Width | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.1 | Marking | Yes | Mandatory | d) Length of the tape on each roll; | Satisfactory/Unsatisfactory | Nominal length | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Quantitative | 3.1 | Marking | Yes | Mandatory | e) Nominal thickness of the tape; | Satisfactory/Unsatisfactory | Nominal thickness | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | Marking | Yes | Mandatory | f) Number of rolls in the unit pack or larger package; | Satisfactory/Unsatisfactory | Quantity | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | Marking | Yes | Mandatory | g) 'This side up' or a similar indication, appropriately positioned, so that the rolls of tape will be lying flat on their cut edges, this designation is not needed on spindle-packed type; | Satisfactory/Unsatisfactory |  | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | Marking | Yes | Mandatory | h) Manufacturer's or supplier's identification mark clearly marked on the core of the roll, this mark shall include the batch number; | Satisfactory/Unsatisfactory | Batch number | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | Marking | Yes | Mandatory | j) Customer's identification, if any; | Satisfactory/Unsatisfactory |  | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | Marking | Yes | Mandatory | k) Country of manufacture | Satisfactory/Unsatisfactory |  | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | Marking | Yes | Mandatory | m) Date of despatch by the manufacturer; | Satisfactory/Unsatisfactory | Month and year of manufacture | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | Marking | Yes | Mandatory | n) Date of expiry. | Satisfactory/Unsatisfactory | The declared month and year of expiry, if applicable. | 9 | 7809 Part 1 (1975)
7809 | 3 | 1 | 1986 | 2 | PRESSURE SENSITIVE ADHESIVE INSULATING TAPES FOR ELECTRICAL PURPOSES | Electrical | Qualitative | 3.1 | Marking | Yes | Mandatory | 9.1.1 The product may also be marked with Standard mark. | Satisfactory/Unsatisfactory |  | 9.1.1 | 7809 Part 1 (1975)