## IS14255_0_0_1995_1_TestReport
Annex-C
IS Number | Part | Section | Year | Number of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause/ Table/ Annex Reference | Test Parameter Name | To be tested by Lab (YES / NO) | Mandatory or Optional | Characteristics (as per Indian Standard) - No specified values to be mentioned here | Test Result/ Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference | Sample Quantity | Equipment |  | Specified Limit for Grade H2 | Specified Limit for Grade H2 | Specified Limit for Grade H4 | Specified limits for Tensile strength of XLPE insulation | Specified limits for Tensile strength of XLPE insulation | Specified Limits for Elongation at break of XLPE insulation | Specified Limits for Elongation at break of XLPE insulation | Specified limit for tensile strength variation after ageing in air oven | Specified limit for tensile strength variation after ageing in air oven | Specified limit for Elongation variation after ageing in air oven | Specified Elongation variation after ageing in air oven | Specified limit for Elongation under load at hot-set condition | Specified limit for Elongation under load at hot-set condition | Specific requirement for Permanent elongation (set) after cooling | Specific requirement for Permanent elongation (set) after cooling | Specific Requirement for Shrinkage of insulation | Specific Requirement for Shrinkage of insulation | Specified Requirement for Water absorption | Specified Requirement for Water absorption | Specified Requirement for volume resistivity at 27 degree XLPE | Specified Requirement for volume resistivity at 27 degree XLPE | Specified Requirement for volume resistivity at 70 degree XLPE insulation | Specified Requirement for volume resistivity at 70 degree XLPE insulation | Specified Requirement for volume resistivity at 27 degree PE | Specified Requirement for volume resistivity at 27 degree PE | Specified Requirement for volume resistivity at 70 degree PE insulation | Specified Requirement for volume resistivity at 70 degree PE insulation | Specified Requirement for Tensile strength of PE insulation | Specified Requirement for Tensile strength of PE insulation | Specified Requirement for Elongation at break PE insulation | Specified Requirement forElongation at break PE insulation | Specified Requirement for Melt flow index PE | Specified Requirement for Melt flow index PE | Specified Requirement for Vicat softening point of PE insulation, | Specified Requirement for Vicat softening point of PE insulation, | Specified Requirement of resistance test on phase / street light conductor of nomical area 16 sq mm | Specified Requirement of resistance test on phase / street light conductor of nomical area 16 sq mm a | Specified Requirement of resistance test on phase / street light conductor of nomical area 25 sq mm | Specified Requirement of resistance test on phase / street light conductor of nomical area 25 sq mm | Specified Requirement of resistance test on phase / street light conductor of nomical area 35 sq mm | Specified Requirement of resistance test on phase / street light conductor of nomical area 35 sq mm | Specified Requirement of resistance test on phase / street light conductor of nomical area 50 sq mm | Specified Requirement of resistance test on phase / street light conductor of nomical area 50 sq mm | Specified Requirement of resistance test on phase / street light conductor of nomical area 70 sq mm | Specified Requirement of resistance test on phase / street light conductor of nomical area 70 sq mm | Specified Requirement of resistance test on phase / street light conductor of nomical area 95 sq mm | Specified Requirement of resistance test on phase / street light conductor of nomical area 95 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 16 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 16 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 25 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 25 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 35 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 35 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 50 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 50 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 70 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 70 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 95 sq mm | Specified Requirement of breaking load for messenger conductor of nomical area 95 sq mm | Specified Requirement of messenger conductor resistance test for messenger conductor of nomical area 16 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 16 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 25 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 25 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 35 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 35 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 50 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 50 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 70 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 70 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 95 sq mm | Specified Requirement of messenger conductor resistance test of nomical area 95 sq mm | If the test is quantitative, the Min and Max value to be written after applying the tolerance given in the standard. If only upper and lower limit is given, mention ONLY Min or ONLY Max balue and leave the other cell blank. If the test is Qualitative, both Only Min column to be filled by the qualitiative requirement, the Max column to be left blank
THIS ROW TO BE LEFT BLANK | [20 empty] | Min | Max | Min | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Clause 4.1 | Phase/Strect Lighting Conductor | YES | Mandatory | H2 grade (Tensile Strength-Above 100 and Upto & including 150)/H4 grade (Tensile Strength-Above 150) | N/mm2, value upto 2 decimal places, No of observations - Not specified | AluMinum grade (H2 / H4) | Clause 4.1 | IS 8130 |  |  |  |  | 100 | 150 | 150
[5 empty] | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Clause 4.1 | Phase/Strect Lighting Conductor | YES | Mandatory | Aluminium shall comply with requirements of IS 8130:1984 | To be checked on declaration basis | Aluminium shall comply with requirements of IS 8130:1984 | [5 empty] | Manufacturer need to provide wire before stranding
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Chemical,Electrical | Qualitative | Clause 4.2 | Messenger (Neutral Conductor or Otherwise) | YES | Mandatory | The conductor shall be of heat treated alumiinium magnisium- silicon alloy wires containing approximate 0.5% magnesium and approximately 0.5 % silicon conforMing to IS 398 (Part 4) | To be checked on declaration basis | Diameter of aluminium alloy wire used |  | IS 398(Part 4) |  |  |  | Manufacturer need to provide wire before stranding
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | Clause 5.1 | Insulation | YES | Mandatory | The insulation shall be either of cross-linked polyethylene compound or of polyethylene compound | To be checked on declaration basis | Type of insulation material (XLPE / PE) | cl 5.1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 (i) | Tensile strength XLPE insulation, | Yes | Mandatory | Tensile strength of XLPE insulation,N/mm2, Min | (No of decimal places- 1, No of observations - Not specified) |  |  | IS 10810 (Part 7) | 1 | [6 empty] | 12.5
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 (ii) | Elongation at break XLPE insulation, | Yes | Mandatory | Elongation at break of XLPE insulation, %, Min | % , (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 7) | 2 | [8 empty] | 200
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 (iii) b | Ageing tensile variation XLPE, | Yes | Mandatory | Tensile strength variation after ageing in air oven, %, Max | % , (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 11) | [12 empty] | 25
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 (iii) c | Ageing elongation variation XLPE, | Yes | Mandatory | Elongation variation after ageing in air oven, , %, Max | % , (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 11) | [14 empty] | 25
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 (iv) b | Hot set elongation XLPE | Yes | Mandatory | Elongation under load at hot-set condition , %, Max | % , (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 30) | [16 empty] | 175
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 (iv) c | Hot set permanent set XLPE, | Yes | Mandatory | Permanent elongation (set) after cooling, %, Max | % , (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 30) | [18 empty] | 15
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 (v) b | Shrinkage XLPE | Yes | Mandatory | Shrinkage of insulation, , %, Max | % , (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 12) | [20 empty] | 4
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 (vi) b | Water absorption XLPE | Yes | Mandatory | Water absorption, mg/cm², Max | (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 33) | [21 empty] | 1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 (vii) a | Volume resistivity XLPE at 27°C | Yes | Mandatory | Volume resistivity at 27 °C, 10¹³ ohm-cm, Min | (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 43) | [23 empty] | 1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 (vii) b | Volume resistivity XLPE at 70°C | Yes | Mandatory | Volume resistivity at 70 °C, 1011 ohm-cm, Min | (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 43) | [25 empty] | 1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Chemical | Quantitative | Table 1 (Properties of XLPE insulation),Clause 5.1 | carbon black: a) content b) Dispersion | Yes | optional | Under consideration | Under consideration
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 2 ( Property of PE insulation) clause 5.1 | Volume resistivity PE at 27°C | Yes | Mandatory | Volume resistivity PE at 27°C, 1014 ohm-cm, Min | (No of decimal places- 0, No of observations - Not specified) | [30 empty] | 1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 2 ( Property of PE insulation) clause 5.1 | Volume resistivity PE at 70°C | Yes | Mandatory | Volume resistivity PE at 70°C 1012 ohm-cm, Min | (No of decimal places- 0, No of observations - Not specified) | [32 empty] | 1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 2 ( Property of PE insulation) clause 5.1 | Tensile strength PE insulation | Yes | Mandatory | Tensile strength of PE insulation N/mm², Min | (No of decimal places- 1, No of observations - Not specified) |  |  | IS 10810 (Part 7) | [31 empty] | 10
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 2 ( Property of PE insulation) clause 5.1 | Elongation at break PE insulation | Yes | Mandatory | Elongation at break of PE insulation, % , Min | % , (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 7) | [33 empty] | 300
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 2 ( Property of PE insulation) clause 5.1 | Melt flow index PE | Yes | Mandatory | Melt flow index of PE insulation, Max | (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 23) | [36 empty] | 3
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | Table 2 ( Property of PE insulation) clause 5.1 | Vicat softening point PE | Yes | Mandatory | Vicat softening point of PE insulation, °C, Min | (No of decimal places- 0, No of observations - Not specified) |  |  | IS 10810 (Part 22) | [37 empty] | 85
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Chemical | Quantitative | Table 2 ( Property of PE insulation) clause 5.1 | carbon black: a) content b) Dispersion | Yes | optional | Under consideration | Under consideration
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | Table 2 ( Property of PE insulation) clause 5.1 | Environmental stress cracking PE | Yes | Mandatory | No cracks shall be visible to naked eye | Satisfactory/ Unsatisfactory |  |  | IS 10810 (Part 29)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 6.1 | Conductor | YES | Mandatory | The power/outer insulated neutral/street lighting conductors shall conform to flexibility class 2 of IS 8130 : 1984. | Satisfactory/ Unsatisfactory | Conductor size & class (Flexibility class 2 as per IS 8130:1984) | Cl. 6.1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 6.2 | Conductor | YES | Mandatory | The messenger (Neutral conductor) or otherwise shall be either stranded circular or compacted circular type | Stranded circular type/ compacted circular type | Messenger conductor construction details | Cl. 6.2 |  | 1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 6.2 | Conductor | YES | Mandatory | The messenger (Neutral conductor) or otherwise shall have Minimum 7 strands. , Min | 7 Strands/ less than 7 strands/ more than 7 strands | Number of strands (Minimum 7 strands) | Cl. 6.2 |  | 2
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 6.2 | Conductor | YES | Mandatory | The surface of the conductor shall be smooth. | Satisfactory/ Unsatisfactory | Surface condition of messenger conductor | Cl. 6.2 |  | 3
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 6.3 | Conductor | YES | Mandatory | A protective barrier may be applied between the conductor and insulation, if required. Such barrier, when used, shall be compatible with insulating material and suitable for the operating temperature of the cable. | Satisfactory/ Unsatisfactory/ Not Applicable | Type of protective barrier & insulation material | Cl. 6.3
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 6.4 | Conductor | YES | Mandatory | The size of street lighting conductor shall be 16 mm². | Please mention size of Condcutor | Conductor size (16 mm²) | Cl. 6.4
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 6.5 | Conductor | YES | Mandatory | The size of messenger conductor shall be 16/25/35/50/70/95 , Sqmm | Sqmm , (No of decimal places- 0, No of observations - Not specified) | Messenger conductor size (as per Table 3) | Cl. 6.5
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 6.6 | Conductor | YES | Mandatory | There shall be no joints in any wire of the messenger conductor except those made in the base rod or wires before final drawing. | Satisfactory/Unsatisfactory | Manufacturing process of messenger conductor | Cl. 6.6
|  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 6.6 | Conductor | YES | Mandatory | The direction of outer layer of wires in messenger conductor shall be right hand. | Satisfactory/Unsatisfactory | Lay direction of outer layer (right-hand lay) | Cl. 6.6
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 7.1, Table 4 | Thickness of insulation | Yes | Mandatory | The conductor (with protective barrier, wherever applied) shall be provided with crosslinked polyethylene or polyethylette insulation applied by extrusion. | Satisfactory/ unsatisfactory | insulation application process |  | IS 10810 (Part 8)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 7.2 & Table 4 | Thickness of insulation | Yes | Mandatory | The average thickness of insulation shall be not less than the nomiual value (ti) specified in Table 4., mm, Min | mm, (No of decimal places- 1, No of observations - 18) | Conductor size |  | IS 10810 (Part 8)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 7.3 | Tolerance on Thickness of Insulation | Yes | Mandatory | The smallest of measured values of thickness of insulation shall not fall below the noMinal value specified in Table 4 by more than (0.1 mm + 0.1 NoMinal Thickness(ti)). mm Min | (No of decimal places- 2, No of observations - 1) | Conductor size |  | IS 10810 (Part 8)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 7.4 | Application of insulation | Yes | Mandatory | The insulation shall be so applied that it fits closely on the conductor (or barrier, if any) | Satisfactory/ Unsatisfactory |  | Cl. 7.4 |  | 1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 7.4 | Application of insulation | Yes | Mandatory | it shall be possible to remove insulation without damaging the conductor. | Satisfactory/ Unsatisfactory |  | Cl. 7.4 |  | 2
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 7.5 | Application of insulation | Yes | Mandatory | The colour of insulation shall be black. | Satisfactory/ Unsatisfactory |  | Cl. 7.5
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantative | 8 | Core identification | Yes | Mandatory | Tbe phase conductors shall be provided with one, two or three ‘ridges’ | One/two/three/more then three(mention the number) |  | Cl. 8
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantative | 8.1 | Core identification | Yes | Mandatory | outer neutral insulated conductor, if provided, shall have four ‘ridges’ as shown in Fig. 1 for quick identification. | Satisfactory/ Unsatisfactory |  | Cl. 8 |  | 1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantative | 8.1 | Core identification | Yes | Mandatory | Street lighting and messenger conductors shall have no identification marks. | Satisfactory/ Unsatisfactory | Applicable only if neutral conductor is provided | Cl. 8.1 |  | 2
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantative | 8.2 | Core identification | Yes | Mandatory | The single phase conductor shall be provided with 'One Ridge' and if neutral insulated conductor is provided shall have 'Four Ridges' as shown in Fig. 1 for quick identification. The Street Light Conductor & Messenger Conductor (if insulated) shall not have any identification mark | Satisfactory/ Unsatisfactory |  | Cl.8.2
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantative | 8.3 | Core identification | Yes | Mandatory | Identification by other means, as agreed between the supplier and purchaser, is also permissible. | Satisfactory/ Unsatisfactory | Declaration regarding core identification required as agreed between supplier and purchaser-if applicable | Cl. 8.3
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 9.1 | Assembly (Laying up) | Yes | Mandatory | Three insulated phase couductors, one insulated neutral conductor (if required) and a street lighting conductor (if required) shall be twisted around the bare (or insulated) as required messenger conductor without fillers | Satisfactory/ Unsatisfactory |  | Cl. 9.1 |  | 1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 9.1 | Assembly (Laying up) | Yes | Mandatory | lay not exceeding 3.5 times the diameter of the insulated phase conductor. | Satisfactory/ Unsatisfactory |  | Cl. 9.1 |  | 2
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 9.2 | Assembly (Laying up) | Yes | Mandatory | Single insulated phase conductor, one insulated neutral conductor (if required) and a Street Lighting Conductor (if required) shall be twisted around the bare ( or insulated) as required Messenger Conductor without filler with a lay not exceeding 35 times the diameter of the insulated phase conductor. | Satisfactory/ Unsatisfactory |  | Cl. 9.2
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 9.3 | Assembly (Laying up) | Yes | Mandatory | The direction of lay shall be right-hand. | Satisfactory/ Unsatisfactory |  | Cl. 9.3
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(a) (i) | Tensile test on phase & street light conductor | Yes | Mandatory | H2 grade (Tensile Strength-Above 100 and Upto & including 150)/H4 grade (Tensile Strength-Above 150). 95 % if wire taken from finished conductor, N/mm2 | , value upto 2 decimal places, No of observations - Not specified | Conductor size & class |  | IS 10810 (Part 2)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 10.1(a) (ii) | Wrapping test on phase & street light conductor | Yes | Mandatory | No visible cracks after wrapping test | Satisfactory/ Unsatisfactory |  |  | IS 10810 (Part 3)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(a) (iii) | Resistance test on phase / street light conductor | Yes | Mandatory | Resistance of the conductor within the limits specified in IS 8130 | , value upto 3 decimal places, No of observations - Not specified |  |  | IS 10810 (Part 5) | [40 empty] | 1.91 |  | 1.2 |  | 0.868 |  | 0.641 |  | 0.443 |  | 0.32
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(b) (i) | Breaking load of messenger conductor, | Yes | Mandatory | Breaking load of messenger conductor, Min, kN | value upto 1 decimal places, No of observations - Not specified |  |  | IS 10810 (Part 2) | [51 empty] | 7 |  | 7 |  | 7 |  | 9.8 |  | 14 |  | 19.7
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(b) (ii) | Elongation test on messenger conductor | Yes | Mandatory | Elongation of specimen shall not be less than 4 percent on a gauge length of 200 mm | (No of decimal places- 0, No of observations - Not specified) |  | Cl 11.3
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(b) (iii) | Resistance test on messenger conductor | Yes | Mandatory | Resistance of messenger conductor as specified in Table 3, Max, Ohm/km | value upto 3 decimal places, No of observations - Not specified | Messenger conductor size & length | Cl 11.3 | IS 10810 (Part 5) | [64 empty] | 1.38 |  | 1.38 |  | 1.38 |  | 0.986 |  | 0.689 |  | 0.492
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(c) (i) | Tensile strength and elongation at break test for XLPE Insulation | Yes | Mandatory | Tensile strength of XLPE Insulation as specified in Table 1 | The tensile strength of XLPE insulation (as per Table 1) are Achieved / Not Achieved |  |  | IS 10810 (Part 5)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(c) (i) | Tensile strength and elongation at break test for XLPE Insulation | Yes | Mandatory | elongation at break of XLPE Insulation as specified in Table 1 | elongation at break of XLPE insulation (as per Table 1) are Achieved / Not Achieved |  |  | IS 10810 (Part 7)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1 (c) (ii) | Ageing in air oven test for XLPE Insulation | Yes | Mandatory | Tensile strength and elongation after ageing of XLPE insulation as specified in Table 1 | The tensile strength and elongation after ageing of XLPE insulation (as per Table 1) are Achieved / Not Achieved |  |  | IS 10810 (Part 11)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(c) (iii) | Hot set test for XLPE Insulation | Yes | Mandatory | Hot set elongation and permanent set of XLPE insulation as specified in Table 1 | The hot set elongation and permanent set of XLPE insulation (as per Table 1) are Achieved / Not Achieved |  |  | IS 10810 (Part 30)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1 (c) (iv) | Shrinkage test for XLPE Insulation | Yes | Mandatory | Shrinkage of XLPE insulation as specified in Table 1 | The shrinkage of XLPE insulation (%) (as per Table 1) is Achieved / Not Achieved |  |  | IS 10810 (Part 12)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1 (c) (v) | Water absorption (Gravimetric) test for XLPE Insulation | Yes | Mandatory | Water absorption of XLPE insulation as specified in Table 1 | The water absorption of XLPE insulation (%) (as per Table 1) is Achieved / Not Achieved |  |  | IS 10810 (Part 33)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1 (c) (vi) | Carbon black test for XLPE Insulation: 1. Content 2. Dispersion | Yes | Mandatory | Under consideration | not applicable
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(d) (i) | Tensile strength and elongation at break test for PE insulation | Yes | Mandatory | Tensile strength and elongation at break of PE insulation as specified in Table 2 | The tensile strength and elongation at break of PE insulation (as per Table 2) are Achieved / Not Achieved |  |  | IS 10810 (Part 7)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(d) (ii) | Melt flow index test for PE insulation | Yes | Mandatory | Melt flow index of PE insulation as specified in Table 2 | The melt flow index of PE insulation (as per Table 2) is Achieved / Not Achieved |  |  | IS 10810 (Part 23)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(d) (iii) | Carbon black test for PE Insulation: 1. Content 2. Dispersion | Yes | Mandatory | Content and dispersion of carbon in PE insulation as specified in Table 2 | under consideration |  |  | IS 10810 (Part 32)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(d) (iv) | Vicat softening point test for PE insulation | Yes | Mandatory | Vicat softening point of PE insulation as specified in Table 3 | The Vicat softening point of PE insulation (as per Table 3) is Achieved / Not Achieved |  |  | IS 10810 (Part 22)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(d) (v) | Environmental stress cracking for PE insulation | Yes | Mandatory | Resistance to crack formation under mechanical stress and chemical exposure of PE insulation as specified in Table 2 | The environmental stress cracking resistance of PE insulation (as per Table 2) is Achieved / Not Achieved |  |  | IS 10810 (Part 29)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1 | Test for thickness insulation | Yes | Mandatory | Insulation thickness of PE Insulation as specified in Table 2 | The insulation thickness of PE insulation (as per Table 2) is Achieved / Not Achieved |  |  | IS 10810 (Part 6)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Quantitative | 10.1(f) | Insulation resistance (Volume resistivity) test | Yes | Mandatory | Volume resistivity of insulation material of PE Insulation as specified in Table 1 & 2 | The volume resistivity of PE insulation (as per Table 4) is Achieved / Not Achieved |  |  | IS 10810 (Part 43)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 10.1(g) | High voltage test at room temperature | Yes | Mandatory | The cable shall withstand a voltage of 3 kV ac (rms) at a frequency of 40 to 60 Hz or a dc voltage of 7.2 kV between conductors for 5 Minutes. | Withstand-3 kV for ac (rms) at a frequency of 40 to 60 Hz or a dc voltage of 7.2 kV between conductors for 5 Minutes/Not withstand - if not withstand at the same. |  |  | IS 10810 (Part 45)
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 11.4 | Bending Test on the Completed Cable | Yes | Mandatory | The test shall be performed on a sample of complete cable. The sample shall be bent around a test mandrel at roonl teulyeraturr for at least one coinplete turn. It shall then be unwound aud the process shall be repeated after turuing the salnyle around its axis by 180 degrees. The cycle of these operatious shall theu be repeated twice. | No cracks visible to the naked eye are allowed |  | Cl.11.4
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 12.1 | Manufacturer's Identification | Yes | Mandatory | The manufacturer shall be identified throughout the length of the cable by means of a tape bearing the manufacturers name or trade-mark and year of lnanufacture. In case the above inethod cannot be employed, or if the purchaser so desires, colour identiticatiou threads in accordance with a scheme to be approved by the Bureau of Iudiau Staudards (BIS) shall be employed. | Marked/Not marked/masked/Not Legible |  | Cl.12.1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 12.2 | Cable Identification | Yes | Mandatory | Cables with cross-linked polyethylene insulation shall be identified throughout the length of the cable by the legend ‘XLPE 90’ aud year of manufacture by a yriuted tape. No identificatiou is required for polyethyleue insulation. | Marked/Not marked/masked/Not Legible |  | Cl.12.2
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.1 | PACKING AND MARKING | Yes | Mandatory | The cable shall be wound on a drum (see IS 10418 : 1982) of suitable size and packed. The ends of the cable shall be sealed by non-hygroscopic material. | Satisfactory/Not satisfactory |  | Cl.13.1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | The cable shall carry the following information either stencilled on the drum or contained in label attached to it | please see below |  | Cl.13.2
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | a)Reference to this Indian Standard, for example,Ref IS 14255 ; | Marked/Not marked/masked/Not Legible |  | Cl.13.2 |  | 1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | b)Manufacturer’s name or trade-mark; | Marked/Not marked/masked/Not Legible |  | Cl.13.2 |  | 2
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | c)Type of cable and voltage grade; | Marked/Not marked/masked/Not Legible |  | Cl.13.2 |  | 3
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | d) No Minal cross-sectional area of phase conductor; | Marked/Not marked/masked/Not Legible |  | Cl.13.2 |  | 4
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | e) Length of cable on the drum; | Marked/Not marked/masked/Not Legible |  | Cl.13.2 |  | 5
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | f) Number of lengths on the drum (if more than one) | Marked/Not marked/masked/Not Legible |  | Cl.13.2 |  | 6
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | g) Direction of rotation of drum (by means of an arrow); | Marked/Not marked/masked/Not Legible |  | Cl.13.2 |  | 7
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | h) Gross mass; | Marked/Not marked/masked/Not Legible |  | Cl.13.2 |  | 8
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | j) Country of manufacture; and | Marked/Not marked/masked/Not Legible |  | Cl.13.2 |  | 9
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2 | PACKING AND MARKING | Yes | Mandatory | j) Year of manufacture | Marked/Not marked/masked/Not Legible |  | Cl.13.2.1 |  | 10
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical | Qualitative | 13.2.1 | PACKING AND MARKING | Yes | Mandatory | The cable (drum or label) may also he marked with the Standard mark. | Marked/Not marked/masked/Not Legible |  | Cl.13.2.1
14255 |  |  | 1995 | 1 | AERIAL BUNCHED CABLES - FOR WORKING VOLTAGES UP TO AND INCLUDINS; 1 100 VOLTS - SPECIFICATION | Electrical |  | 14 | ACCESSORIES FOR AERIAL BUNCHED CABLES | No |  | The accessories which are in common use for aerial bunchhed cables are under consideration. | Under consideration |  | Cl 14

## IS14255_0_0_1995_1_TestRequest
Grade of Phase/Street light conductor | Diameter of aluminium alloy wire used for messenger(mm) | Type of insulation material | Conductor size as per IS 8130 | class (Flexibility class 2 as per IS 8130 | Messenger conductor construction details | Messenger conductor size (as per Table 3) in mm2
H2 | 2 | cross-linkrd polycthylrnc comnpound (XLPE) | As declared | As declared | Stranded circular | 16
H4 | 2.5 | polycthylene compound(PE) |  |  | compacted circular | 25
| 2.89 |  |  |  |  | 35
| 3.15 |  |  |  |  | 50
| 3.31 |  |  |  |  | 70
| 3.4 |  |  |  |  | 95
3.45
3.55
3.66
3.71
3.81
3.94
4
4.26