## TRep - Review
IS Number | Part | Section | Year | Number of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause/ Table/ Annex Reference | Test Parameter Name | To be tested and/or reported by Lab (Yes/No) | Mandatory or Optional | Requirement (as per Indian Standard) | Expressive Test Result/ Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference |  |  |  | Remarks | Extinguishing medium Water & Water Mist | Extinguishing medium Water & Water Mist | Extinguishing medium Carbon DIoxide | Extinguishing medium Carbon DIoxide | Extinguishing medium Clean Agents | Extinguishing medium Clean Agents | Extinguishing medium Powders | Extinguishing medium Powders | Extinguishing medium Foam | Extinguishing medium Foam | Low pressure extinguishers | Low pressure extinguishers | Class A - 1A | Class A - 1A | Class A - 2A | Class A - 2A | Class - 3A | Class - 3A | Class - 4A | Class - 4A | Class - 6A | Class - 6A | Class - 10A | Class - 10A | Class - 15A | Class - 15A | Class - 20A | Class - 20A | Class - 8B | Class - 8B | Class - 13 B | Class - 13 B | Class - 21B | Class - 21B | Class - 34B | Class - 34B | Class - 55B | Class - 55B | Class - 70B | Class - 70B | Class - 89B | Class - 89B | Class - 113B | Class - 113B | Class - 144B | Class - 144B | Class - 183B | Class - 183B | Class - 233B | Class - 233B | Carbon Content | Carbon Content | Sulphur Content | Sulphur Content | Phosphorous content | Phosphorous content
[22 empty] | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Qualitative | Clause 4 | Type of extinguishers | Yes | Mandatory | Type of extinguishers (Water based/Foam Based/Powders/Carbondioxide/Clean agents/Water mist type) | To be checked based on declaration basis | a) Declaration regarding types of fire extinguishers medium. b) If it is water based type, then declaration regarding whether it is pure water or water with additives c) If it is water based type, then declaration regarding whether the powders may contain ABC/BC/D Type | Clause 4 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Qualitative | Clause 5.1.1 | Type of extinguishing medium | Yes | Mandatory | Type of extinguishing medium | To be checked based on declaration basis | Type |  | On declaration basis of material |  |  |  |  | Separate test report format to be prepared for IS 15222, IS 4308 & IS 4989) | Satisfactory/Unsatisfactory (Extinguishing Media is not water and water mist) | Satisfactory/Unsatisfactory (Extinguishing Media is not water and water mist) | Please see the test report of IS 15222 |  | Satisfactory/Unsatisfactory (Extinguishing Media is not Clean Agent or Clean agent name is not marked on label) |  | Please see the test report of IS 4308. |  | Please see the test report of IS 4989
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Qualitative | Clause 5.2 | Propellants | Yes | Mandatory | The propellants for stored pressure and cartridge operated extinguishers shall be air, carbon dioxide and nitrogen. | To be checked based on declaration basis | Declaration regarding propellant used (air / CO₂ / nitrogen) | Clause 5.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 5.3.1 | Fill Density | Yes | Mandatory | Fill Density, kg/l, Max | Values upto 3 decimal places | Type | Cl 5.3.1 | IS 15683 | [8 empty] | 0.667 kg/l | To be checked based on declaration basis
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 5.3.2 | Filling Tolerance | Yes | Mandatory | Filling Tolerance, percent |  | Type | Clause 5.3.2 | IS 15683 | [5 empty] | Satisfactory/Unsatisfactory (Tolerance is not within 0 to 5 percent by volume) |  | Satisfactory/Unsatisfactory (Tolerance is not within 5 to 0 percent by mass) |  | Satisfactory/Unsatisfactory (Tolerance is not within 0 to 5 percent by mass) |  | Satisfactory/Unsatisfactory (Tolerance is not within -2 to 2 percent by volume) |  | Satisfactory/Unsatisfactory (Tolerance is not within 0 to 5 percent by volume)
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | Clause 5.3.3 | Capacities | Yes | Mandatory | Capacity | Value to be specified in integers or whole numbers. To be checked based on declaration basis | Type | Clause 5.3.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 6.1 | Test Pressure (Pt) | Yes | Mandatory | Test Pressure (Pt), Mpa | Value upto 1 decimal place | Decalaration of low pressure or high pressure extinguishers | Clause 6.1 | IS 15683 | [15 empty] | 3.5 | 1.43 x P ms
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 6.2 | Burst Pressure (Pb) | Yes | Mandatory | Burst Pressure (Pb), MPa | Unit of measurement-MPa - Number of decimal places - Integer value only | Type | Clause 6.2 | IS 15683 |  |  |  |  | The value of P ms to be calculated in other requirement and then the P ms value to be used to find out Max value test pressure. | [10 empty] | 5.5 | 2.7 x P ms
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 7.1 | Operating Temperature Ranges | Yes | Mandatory | Operating Temperature Ranges (5°C to + 60°C or 0°C to + 60°C or − 10°C to + 60°C or − 20°C to + 60°C or − 30°C to + 60°C) | To be checked based on declaration basis | Operating Temperature Ranges | Clause 7.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Cl 7.2 | Effective discharge time | Yes | Mandatory | Effective discharge time, s, Min | Value to be specified in integers or whole numbers | Class type and sub class | Cl 7.2 | IS 15683 | 1 | [16 empty] | 8 |  | 13 |  | 13 |  | 13 |  | 13 |  | 13 |  | 13 |  | 13 |  | 8 |  | 8 |  | 8 |  | 8 |  | 9 |  | 9 |  | 9 |  | 12 |  | 15 |  | 15 |  | 15
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Cl 7.2 | Bulk range | Yes | Mandatory | Bulk range, m, Min | Value upto 1 decimal place | Class type and sub class | Clause 7.2.3 | IS 15683 | 2 | [16 empty] | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 1 |  | 1 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.3.1 | Resistance to Temperature Changes | Yes | Mandatory | Shall operate as intended | Satisfactory/Unsatisfactory (Not operated as intended) | Type | Clause 7.3.2 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.3.1 | Resistance to Temperature Changes | Yes | Mandatory | Time to commence discharge, s | Value to be specified in integers or whole numbers | Type | Clause 7.3.2 | IS 15683 | 2 | [17 empty] | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | 7.3.1 | Resistance to Temperature Changes | Yes | Mandatory | Following cycle 1, Retention of initial charge, % | Value to be specified in integers or whole numbers | Type | Clause 7.3.2 | IS 15683 | 3 | [17 empty] | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | 7.3.1 | Resistance to Temperature Changes | Yes | Mandatory | Following cycle 2, Retention of initial charge, % | Value to be specified in integers or whole numbers | Type | Clause 7.3.2 | IS 15683 | 4 | [17 empty] | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.4.1.1 | Retention of Charge | Yes | Mandatory | Fire extinguishers shall be fitted with a control valve allowing the discharge of the extinguishing medium to be interrupted at any time | Satisfactory/Unsatisfactory (Not fitted with a control valve allowing the discharge of the extinguishing medium to be interrupted at any time) | Type | 7.4.1.1 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.4.1.1 | Retention of Charge | Yes | Mandatory | The extinguisher shall be adequately resistant to leakage | Satisfactory/Unsatisfactory (The extinguisher in not adequately resistant to leakage) | Type | Clause 7.4.2 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | 7.4.1.1 | Retention of Charge | Yes | Mandatory | The second pressure/weight of contents as appropriate shall be no less than 75 percent of the first, after interruption of the discharge, %, Min | Value to be specified in integers or whole numbers | Type | Clause 7.4.1.2 | IS 15683 | 3 | [16 empty] | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75 |  | 75
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.5.1 | Impact Resistance Test | Yes | Mandatory | The extinguisher shall not release pressure in a potentially dangerous manner | Satisfactory/Unsatisfactory (extinguisher released pressure in a potentially dangerous manner) | Type | 7.5.1.2 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.5.1 | Impact Resistance Test | Yes | Mandatory | The extinguisher shall be judged fit and proper | Satisfactory/Unsatisfactory (evidence of bursting, breakage or ejection of components are found) | Type | 7.5.1.2 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.5.2 | Vibration Resistance Test | Yes | Mandatory | Following exposure to the vibration test, the extinguisher shall comply with the discharge requirements specified | Satisfactory/Unsatisfactory (Following exposure to the vibration test, the extinguisher not complied with the discharge requirements specifiedd) | Type | 7.2 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.5.2 | Vibration Resistance Test | Yes | Mandatory | Vibration Resistance Test - Withstanding exposure to the conditions | Satisfactory/Unsatisfactory (Physical failure of components are observed) | Type | 7.2 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.6.1 | Resistance to Corrosion - External | Yes | Mandatory | The mechanical operation of all working parts shall be unimpaired | Satisfactory/Unsatisfactory (The mechanical operation of all working parts are impaired) | Type | CL 7.6.1 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.6.1 | Resistance to Corrosion - External | Yes | Mandatory | The minimum effective discharge time and bulk range of discharge shall comply with the requirements specified in 7.2 | Satisfactory/Unsatisfactory (The minimum effective discharge time and bulk range of discharge not complied with the requirements after exposure) | Type | CL 7.6.1 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.6.1 | Resistance to Corrosion - External | Yes | Mandatory | The pressure gauge, if one is fitted, shall remain functional and watertight | Satisfactory/Unsatisfactory (The pressure gaugeis not functional and watertight) | Type | CL 7.6.1 | IS 15683 | 3
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.6.1 | Resistance to Corrosion - External | Yes | Mandatory | There shall be no corrosion of the metal of the extinguisher body; discolouration/superficial corrosion of non-ferrous metals is acceptable, but galvanic corrosion between dissimilar metals shall not be permitted. | Satisfactory/Unsatisfactory ( corrosion of the metal of the extinguisher body) | Type | CL 7.6.1 | IS 15683 | 4
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.6.2 | Resistance to Corrosion - Internal | Yes | Mandatory | There shall be no visible signs of corrosion of the metal or detachment, cracking or bubbling | Satisfactory/Unsatisfactory ( There is visible signs of corrosion of the metal or detachment, cracking or bubbling) | Type | CL 7.6.2 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.6.2 | Resistance to Corrosion - Internal | Yes | Mandatory | There shall be no visible change in the colour of extinguishing medium other than that resulting from the thermal cycling in case of water base media only. | Satisfactory/Unsatisfactory ( There is visible change in the colour of extinguishing medium ) | Type | CL 7.6.2 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.7 | Tapping Test | Yes | Mandatory | Portable Extinguisher shall operate satisfactorily |  | Type | Clause 7.7 | IS 15683 | 1 | [10 empty] | Satisfactory/Unsatisfactory (Operation is not satisfactory after test)
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.7 | Tapping Test | Yes | Mandatory | Commence discharge within 5 s of the opening of the control valve |  | Type | Clause 7.7 | IS 15683 | 2 | [10 empty] | Satisfactory/Unsatisfactory (Not Commenced discharge within 5 s of the opening of the control valve)
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 7.7 | Tapping Test | Yes | Mandatory | Not retain more than 15 percent of initial charge within the extinguisher following complete discharge |  | Type | Clause 7.7 | IS 15683 | 3 | [10 empty] | Satisfactory/Unsatisfactory (Retained more than 15 percent of initial charge within the extinguisher following complete discharge)
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | 7.8 | Intermittent Discharge Test | Yes | Mandatory | time from the control valve is opened until the extinguishing media starts to discharge, s, max | Value to be specified in integers or whole number | Type | Clause 7.8 | IS 15683 | 1 | [5 empty] | 5 |  | 5 |  | 5 |  | 5 |  | 5 |  | 5
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | 7.8 | Intermittent Discharge Test | Yes | Mandatory | Percentage retaintion of end of discharge to original charge | Value to be specified in integers or whole number | Type | Clause 7.8 | IS 15683 | 2 | [5 empty] | 10 |  | 10 |  | 10 |  | 15 |  | 10 |  | 10
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | Clause 8.1.1, Table 3 | Fire Rating | Yes | Mandatory | Class A Fire Rating - Powder, kg | Value upto 1 decimal place | Type, Class, Sub-class | Clause 8.3 | 15683 | 1 | [17 empty] | 2 | 2 | 4 | 4 | 6 | 6 | 9 | 9
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | Clause 8.1.1, Table 3 | Fire Rating | Yes | Mandatory | Class A Fire Rating – Water/Foam/Water Mist, l | Value upto 1 decimal place | Type, Class, Sub-class | Clause 8.3 | 15683 | 2 | [18 empty] | 6 | 6 | 10 | 10
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | Clause 8.1.1, Table 3 | Fire Rating | Yes | Mandatory | Class A Fire Rating – Clean Agent, kg | Value upto 1 decimal place | Type, Class, Sub-class | Clause 8.3 | 15683 | 3 | [18 empty] | 6 | 6 | 8 | 8
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | Clause 8.1.2, Table 4 | Class B Fire Rating | Yes | Mandatory | Class B Fire Rating – Powder, kg | Value upto 1 decimal place | Type, Class, Sub-class | Clause 8.4 | IS 15683 | 1 | [37 empty] | 2 | 2 | 3 | 3 | 4 |  |  | 4 | 6 |  |  | 6
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | Clause 8.1.2, Table 4 | Class B Fire Rating | Yes | Mandatory | Class B Fire Rating – Carbon Dioxide, kg | Value upto 1 decimal place | Type, Class, Sub-class | Clause 8.4 | IS 15683 | 2 | [37 empty] | 2 | 3 | 5 | 5
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | Clause 8.1.2, Table 4 | Class B Fire Rating | Yes | Mandatory | Class B Fire Rating – Clean Agent, kg | Value upto 1 decimal place | Type, Class, Sub-class | Clause 8.4 | IS 15683 | 3 | [37 empty] | 2 | 2 | 4 | 4 | 6 |  |  | 6
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | Clause 8.1.2, Table 4 | Class B Fire Rating | Yes | Mandatory | Class B Fire Rating – Foam / Water Mist, l | Value upto 1 decimal place | Type, Class, Sub-class | Clause 8.4 | IS 15683 | 4 | [39 empty] | 3 | 3 | 6 |  |  | 6 | 9 |  |  | 9
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 8.1.4 | Extinguish Test | Yes | Mandatory | Extinguishers recommended as suitable for Class D fires shall extinguish the appropriate test fire or fires. | Satisfactory/Unsatisfactory (Not extinguished the appropriate test fire of Class D) | Type, Class | Clause 8.5 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 8.1.5 | Extinguish Test | Yes | Mandatory | Extinguishers recommended as suitable for Class F fires shall extinguish the appropriate test fires. | Satisfactory/Unsatisfactory (Not extinguished the appropriate test fire of Class F) | Type, Class | Clause 8.6 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Cl.8.1.5 | Splash Test | Yes | Mandatory | Shall pass splash test requirements as described in 8.7 | Satisfactory/Unsatisfactory (failed splash test) | Type, Class | Clause 8.7 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Electrical | Quantitative | CL 8.8 | Electrical Conductivity of Extinguisher Discharge | Yes | Mandatory | When the extinguisher is in operation and the metallic plate is live, the current between the handle or the nozzle and earth and between earth and the extinguisher shall be no more than 0.5 mA at any time during the complete discharge duration of the extinguisher. mA, Max | Value upto 1 decimal places | Type, Class | CL 8.8 | IS 15683 | [6 empty] | 0.5 | [7 empty] | 0.5
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.1 | Construction Requirements -High Pressure Extinguisher | Yes | Mandatory | Extinguishers with a service pressure greater than 19 bar (for example, carbon dioxide type) shall have concave base. | Satisfactory/Unsatisfactory (Without concave base) | Type, Class, Serivce Pressure |  | IS 15683 | 1 |  |  |  | The Treq and Trep formats of referred IS 7385 (Parts 1 and 2) is required to be prepared separatelly in future
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.1 | Construction Requirements -High Pressure Extinguisher | Yes | Mandatory | For carbon dioxide type extinguishers, in case of steel body, it shall conform to IS 7285 (Parts 1 and 2) and in case of aluminium-body, it shall conform to IS 15660. | Please see the Test report of IS IS 7285 (Parts 1 and 2) or IS 15660. | Type, Class, Serivce Pressure |  | IS 15660 | 2 |  |  |  | The Treq and Trep formats of referred IS 15660 & IS 7385 (Parts 1 and 2) is required to be prepared separatelly in future
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.1 | Construction Requirements -High Pressure Extinguisher | Yes | Mandatory | Gas cartridge shall conform to IS 4947 | Please see the Test Report of IS 4947 | Type, Class, Serivce Pressure |  | IS 4947 | 3 |  |  |  | The Treq and Trep formats of referred IS 4947 is required to be prepared separatelly in future
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.1.2 | Construction Requirements - Low Pressure Extinguishers | Yes | Mandatory | A portable extinguisher with a charge exceeding 3 kg shall be constructed such that it can be stood vertically without extra support. | Satisfactory / Unsatisfactory (Not able to stood vertically without extra support.) | Type, Class, Serivce Pressure | Clause 9.2.1.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.1.2 | Construction Requirements - Low Pressure Extinguishers | Yes | Mandatory | Gas cartridge shall conform to IS 4947 | Please see the Test Report of IS 4947 | Type, Class, Serivce Pressure |  | IS 4947 |  |  |  |  | Separate test report format to be prepared for IS 4947
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.1.3 | Construction Requirements - Low Pressure Extinguishers | Yes | Mandatory | Welds and brazed joints shall be free from defects which are prejudicial to the safe use of the cylinder. | Satisfactory / Unsatisfactory (Joint is not free from defects) | Type, Class, Serivce Pressure | Clause 9.2.1.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.1.4 | Construction Requirements - Low Pressure Extinguishers | Yes | Mandatory | Parts attached to the body of the extinguisher shall be manufactured and fitted in a way that minimize concentrations of stress and corrosion risks. | Satisfactory / Unsatisfactory (Parts attached to the body of the extinguisher are not manufactured and fitted in a way that minimize concentrations of stress and corrosion risks.) | Type, Class, Serivce Pressure | Clause 9.2.1.4 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.1.4 | Construction Requirements - Low Pressure Extinguishers | Yes | Mandatory | In the case of welded and brazed parts, the metal shall be compatible with the cylinder material. | Satisfactory / Unsatisfactory ( the metal is not compatible with the cylinder material.) | Type, Class, Serivce Pressure | Clause 9.2.1.4 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.1.5 | Construction Requirements - Low Pressure Extinguishers | Yes | Mandatory | The cylinder manufacturer shall obtain the certificate for the cast analysis of material supplied. | To be checked based on declaration basis | Declaration | Clause 9.2.1.5 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.1.6 | Construction Requirements - Low Pressure Extinguishers | Yes | Mandatory | Threading of palastic components - coarse threads of less than 5 threads/cm or by the use of square-cut threads. | Satisfactory / Unsatisfactory ( more than 5 threads/cm or by not used of square-cut threads) | Type, Class, Serivce Pressure | Clause 9.2.1.6 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.2.1.7 | Construction Requirements - Low Pressure Extinguishers | Yes | Mandatory | Extinguishers that are free standing shall either be fitted with a means to raise the pressure-retaining part of the body at least 5 mm above the floor, or the thickness of metal in the lowest pressure retaining part or parts of the body shall not be less than 1.5 times the minimum thickness of the cylindrical part of the body. | Satisfactory / Unsatisfactory ( Neither be fitted with a means to raise the pressure-retaining part of the body at least 5 mm above the floor, nor the thickness of metal in the lowest pressure retaining part or parts of the body shall not be less than 1.5 times the minimum thickness of the cylindrical part of the body.) | Type, Class, Serivce Pressure | Clause 9.2.1.7 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.2.1.8.2 | Service pressure | Yes | Mandatory | Maximum service pressure (Pms) | To be checked based on declaration basis | Type, Class, Serivce Pressure, Declaration | Cl 9.2.1.8 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.2.2.1 | Burst Test | Yes | Mandatory | The minimum burst pressure (Pb ) shall be 2.7 × Pms but in no case less than 55 bar. | To be checked based on declaration basis | Type, Class, Serivce Pressure, Declaration | Cl 9.2.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.2.2 | Burst Test | Yes | Mandatory | The bursting test shall not cause the cylinder to fragment. | Satisfactory/ Unsatisfactory (cylinder fragmented) | Type, Class, Serivce Pressure, Declaration | Cl 9.2.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.2.3 | Burst Test | Yes | Mandatory | The break shall not show any sign of brittleness, that is the edges of the break shall not be radial but shall be slanting in respect of a diametrical plane and shall exhibit a reduction in area over their entire thickness | Satisfactory / Unsatisfactory (sign of brittleness, radial) | Type, Class, Serivce Pressure, Declaration | Cl 9.2.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.2.4 | Burst Test | Yes | Mandatory | The break shall not show any characterized defect in the metal | Satisfactory / Unsatisfactory (Showed defects in metal after test) | Type, Class, Serivce Pressure, Declaration | Cl 9.2.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.2.5 | Burst Test | Yes | Mandatory | the break shall not occur in any permanent body marking, such as a stamping or engraving | Satisfactory / Unsatisfactory (occured permanent body marking such as stamping or engraving) | Type, Class, Serivce Pressure, Declaration | Cl 9.2.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.2.6 | Burst Test | Yes | Mandatory | During the burst test, no parts shall be ejected from the extinguisher | Satisfactory / Unsatisfactory (Parts ejected from extinguisher) | Type, Class, Serivce Pressure, Declaration | Cl 9.2.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical / Destructive | Qualitative | Clause 9.2.3.2 | Crushing Test | Yes | Mandatory | The extinguishers shall not exhibit any cracks or leaks | Satisfactory / Unsatisfactory (cracked observed) | Type, Class, Serivce Pressure, Declaration | Cl 9.2.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | 9.2.4 | Pressure Cycling Test | Yes | Mandatory | cylinder shall be subjected to and comply with the burst test. | Satisfactory/Unsatisfactory (Cylinder not sustained) | Type, Class, Serivce Pressure, Declaration | Cl 9.2.4 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.2.5.1 | Welded Low Carbon Steel Cylinder - Material | Yes | Mandatory | Welded Low Carbon Steel Cylinder material content | Value upto 2 decimal places | Type, Class, Material | Cl 9.2.5 | IS 15683 | [56 empty] | 0.25 |  | 0.05 |  | 0.05
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.5.2 | Welded Low Carbon Steel Cylinder - Material | Yes | Mandatory | Filler material shall be compatible with the steel to give welds with properties equivalent to those specified for the base sheet. | To be checked based on declaration basis | Type, Class, Material | Cl 9.2.5 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.2.5.3 | Welded Low Carbon Steel Cylinder - Material | Yes | Mandatory | Wall thickness, mm, Min | Value to be specified in integers or whole numbers | Type, Class, Material | Clause 9.2.5.3 | IS 15683 | 1 |  |  |  |  | 0.7 |  | 0.7 |  | 0.7 |  | 0.7 |  | 0.7
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.5.3 | Welded Low Carbon Steel Cylinder - Material | Yes | Mandatory | The cylinder shall have a measured wall thickness greater than the minimum wall thickness | Satisfactory / Unsatisfactory (a measured wall thickness not greater than the minimum wall thickness) | Type, Class, Material | Clause 9.2.5.3 | IS 15683 | 2 |  |  |  |  | 0.7 |  | 0.7 |  | 0.7 |  | 0.7 |  | 0.7
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.6.1 | Stainless Steel Cylinders | Yes | Mandatory | Stainless steel domes and bottoms shall be drawn from fully annealed stock. | To be checked based on declaration basis | Type, Class, Material | Clause 9.2.6.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.2.6.2 | Stainless Steel Cylinders | Yes | Mandatory | Only austenitic stainless steel having a maximum carbon content of 0.03 percent shall be used. | Value upto 2 decimal places | Type, Class, Material | Clause 9.2.6.2 | IS 15683 | [56 empty] | 0.03
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.2.6.3 | Stainless Steel Cylinders | Yes | Mandatory | Wall thickness, mm | Value to be specified in integers or whole numbers | Type, Class, Material | Clause 9.2.6.3 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.6.3 | Stainless Steel Cylinders | Yes | Mandatory | The cylinder shall have a minimum measured wall thickness greater than the minimum wall thickness | Satisfactory / Unsatisfactory (a measured wall thickness not greater than the minimum wall thickness) | Type, Class, Material | Clause 9.2.6.3 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.7.1 | Aluminium cylinder | Yes | Mandatory | Aluminium cylinders shall be of seamless construction | Satisfactory / Unsatisfactory (Not seamless construction) | Type, Class, Material | Clause 9.2.7.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.2.7.2 | Aluminium cylinder | Yes | Mandatory | Wall thickness, mm | Value upto 2 decimal places | Type, Class, Material | Clause 9.2.7.2 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.7.2 | Aluminium cylinder | Yes | Mandatory | Aluminium cylinders shall have a measured wall thickness greater than or equal to the minimum thickness | Satisfactory / Unsatisfactory (a measured wall thickness not greater than the minimum wall thickness) | Type, Class, Material | Clause 9.2.7.2 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.8.1 | Composite Cylinders | Yes | Mandatory | Cylinder shall be made of resin-impregnated or non-impregnated continuous fibres filament-wound over a non-metallic liner | To be checked based on declaration basis | Type, Class, Material | Clause 9.2.8.1 | IS 15683 | 1
[6 empty] | Mechanical | Qualitative | Clause 9.2.8.1 | Composite Cylinders | Yes | Mandatory | The cylinder shall conform to accelerated stress rupture test as given in 9.2.8.4 | Satisfactory / Unsatisfactory (cylinder not conformed to accelerated stress rupture test) | Type, Class, Material | Clause 9.2.8.4 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.8.2 | Composite Cylinders | Yes | Mandatory | The structural reinforced filament material shall be aramid fibre and the impregnation material may be thermosetting or thermoplastic resin. | To be checked based on declaration basis | Type, Class, Material | Clause 9.2.8.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.2.8.3 | Composite Cylinders | Yes | Mandatory | The liner shall be polymeric material. | To be checked based on declaration basis | Type, Class, Material | Clause 9.2.8.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.3 | Carrying Handle | Yes | Mandatory | An extinguisher having a total mass of 1.5 kg or more and having a cylinder diameter of 75 mm or more shall have a carrying handle. | Satisfactory / Unsatisfactory (not having a carrying handle) | Type, Class, Material | Clause 9.3.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.3.2 | Length of carrying handle | Yes | Mandatory | Length of carrying handle for an extinguisher of 7.0 kg or more, mm, min | Value upto one decimal places | Type, Class, Material | Clause 9.3.2 | IS 15683 | 1 |  |  |  |  | 90 |  | 90 |  | 90 |  | 90 |  | 90
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.3.2 | Length of carrying handle | Yes | Mandatory | Length of carrying handle for an extinguisher less than 7.0 kg total mass, mm, min | Value upto one decimal places | Type, Class, Material | Clause 9.3.2 | IS 15683 | 2 |  |  |  |  | 75 |  | 75 |  | 75 |  | 75 |  | 75
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.3.3 | clearance | Yes | Mandatory | clearance between extinguisher body and the carrying handle when the handle is in the carrying position, mm, Min | Value to be specified in integers or whole numbers | Type, Class, Material | Clause 9.3.2 | IS 15683 | [5 empty] | 25 |  | 25 |  | 25 |  | 25 |  | 25
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.4.1 | Mounting | Yes | Mandatory | Each extinguisher intended for wall mounting shall be provided with a means of mounting | To be checked based on declaration basis | Type, Class, Type of Mounting | Clause 9.4.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.4.2 | Mounting | Yes | Mandatory | A wall mounting hook shall require both horizontal and vertical motion of minimum 6 mm to remove the extinguisher from the wall, mm, Min | Value upto one decimal places | Type, Class, Type of Mounting | Clause 9.4.2 | IS 15683 | [5 empty] | 6 |  | 6 |  | 6 |  | 6 |  | 6
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.4.3 | Mounting | Yes | Mandatory | A mounting bracket shall be capable of withstanding a static load of five times the fully charged mass of the extinguisher, when tested in accordance with 9.4.4 | Satisfactory / Unsatisfactory (A mounting bracket not capable of withstanding a static load of five times the fully charged mass of the extinguisher) | Type, Class, Type of Mounting | Clause 9.4.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.4.5 | Mounting | Yes | Mandatory | A mounting bracket equipped with a strap shall not permit the extinguisher to drop to the floor when the strap clamp is opened. | Satisfactory / Unsatisfactory (permiting the extinguisher to drop to the floor when the strap clamp is opened) | Type, Class, Type of Mounting | Clause 9.4.5 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.4.5 | Mounting | Yes | Mandatory | The clamp releasing device shall be of a colour contrasting with that of the immediate extinguisher background and shall be visible. | Satisfactory / Unsatisfactory (clamp releasing device is not colour contrasting with that of the immediate extinguisher background) | Type, Class, Type of Mounting | Clause 9.4.5 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.4.5 | Mounting | Yes | Mandatory | The method of release shall be obvious when viewing the front of the extinguisher. | Satisfactory / Unsatisfactory ( The method of releaseis not obvious when viewing the front of the extinguisher) | Type, Class, Type of Mounting | Clause 9.4.5 | IS 15683 | 3
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.4.6 | Mounting | Yes | Mandatory | A hanger loop shall be located so that the operating instructions face outward when the extinguisher is supported by the mounting means. | Satisfactory / Unsatisfactory (A hanger loop is not located) | Type, Class, Type of Mounting | Clause 9.4.6 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.5.1 | Caps, Valves and Closures | Yes | Mandatory | Cylinder caps, valves and closures shall be designed to provide release of pressure before complete disengagement. | Satisfactory / Unsatisfactory (Cylinder caps, valves and closures is not designed to provide release of pressure before complete disengagement.) | Type, Class | Clause 9.5.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.5.2 | Caps, Valves and Closures | Yes | Mandatory | Threaded connections on cylinder shall have at least four full threads of engagement and be required to relieve pressure with at least two full threads of engagement. | Satisfactory / Unsatisfactory (not having atleast four full threads of engagement) | Type, Class | Clause 9.5.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.5.3 | Caps, Valves and Closures | Yes | Mandatory | The inside diameter of a filling opening for a rechargeable type extinguisher shall be no less than 19 mm except for carbon dioxide (CO2 ) and other gaseous agents extinguishers, mm, Min | Value to be specified in integers or whole numbers | Type, Class | Clause 9.5.3 | IS 15683 | [5 empty] | 19 |  |  |  | 19 |  | 19 |  | 19
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.5.4 | Caps, Valves and Closures | Yes | Mandatory | An extinguisher collar or neck ring with external threads shall have sufficient height so that the cap or valve does not contact the dome or bottom with the gasket removed. | Satisfactory / Unsatisfactory (An extinguisher collar or neck ring with external threads is not having sufficient height) | Type, Class | Clause 9.5.4 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.5.5 | Caps, Valves and Closures | Yes | Mandatory | A cap, valves or closure shall withstand the burst test pressure specified for the cylinder for 1 min without rupture. | Satisfactory / Unsatisfactory (A cap, valves or closure is not withstand the burst test pressure specified for the cylinder for 1 min without rupture) | Type, Class | Clause 9.5.5 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.5.6 | Caps, Valves and Closures | Yes | Mandatory | The edges and surfaces of a fire extinguisher and its mounting bracket shall not be sufficiently sharp to constitute a risk of injury to persons during intended use or while performing maintenance. | Satisfactory / Unsatisfactory (The edges and surfaces of a fire extinguisher and its mounting bracket is sharp to constitute a risk of injury to persons during intended use or while performing maintenance) | Type, Class | Clause 9.5.6 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.5.7 | Caps, Valves and Closures | Yes | Mandatory | Minimum torque value for tightening the cap of extinguisher shall be declared by the manufacturer and it shall be mentioned in the operation manual | To be checked based on declaration basis | To be declared by Manufacturer | Clause 9.5.7 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.6.1 | Safety Devices | Yes | Mandatory | High pressure cylinders and cartridges shall be provided with a safety device in accordance with national regulations. | Satisfactory / Unsatisfactory (High pressure cylinders and cartridges is not provided with a safety device in accordance with national regulations) | Type, Class | Clause 9.6.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.6.2 | Safety Devices | Yes | Mandatory | The operating pressure of the device shall not exceed the test pressure (Pt ) nor be less than the maximum service pressure (Pms ). | Satisfactory / Unsatisfactory (The operating pressure of the device is exceeded the test pressure (Pt ) nor be less than the maximum service pressure (Pms )) | Type, Class | Clause 9.6.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.7.1.1 | Air-Oven Ageing | Yes | Mandatory | Following the exposure, condition the components for 5 h at 27 ± 5 °C and subsequently inspect them for cracking or brittleness. No cracking or brittleness shall be permitted. | Satisfactory / Unsatisfactory (permitting cracking or brittleness) | Type, Class | Clause 9.7.1.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.7.2.2 | Impact Resistance | Yes | Mandatory | No hazardous changes shall occur to the valve assembly such as splinters, fractures or cracks. | Satisfactory / Unsatisfactory (Hazardous changes occured to the valve assembly such as splinters, fractures or cracks) | Type, Class | Clause 9.7.1.2 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.7.2.2 | Impact Resistance | Yes | Mandatory | The valve shall then be capable of withstanding the test pressure (Pt ) without bursting. | Satisfactory / Unsatisfactory (The valve is not capable of withstanding the test pressure (Pt ) without bursting) | Type, Class | Clause 9.7.2.2 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.7.3.2 | Test for Exposure to Extinguishing Medium | Yes | Mandatory | Following the exposure, inspect the component for cracking or brittleness. No cracking or brittleness shall be permitted. | Satisfactory / Unsatisfactory (permitting cracking or brittleness) | Type, Class | Clause 9.7.3.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.8.1 | Hose Assemblies | Yes | Mandatory | Extinguishers having a mass of extinguishing medium greater than 3 kg, or a volume of extinguishing medium greater than 3 litre shall be provided with a flexible discharge hose. | Satisfactory / Unsatisfactory (Extinguishers having a mass of extinguishing medium greater than 3 kg, or a volume of extinguishing medium greater than 3 litre is not provided with a flexible discharge hose) | Type, Class | Clause 9.8.1 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.8.1 | Hose Assemblies | Yes | Mandatory | The length of the flexible section of the hose assembly shall be 400 mm or greater | Satisfactory / Unsatisfactory (The length of the flexible section of the hose assembly is not having 400 mm or greater) | Type, Class | Clause 9.8.1 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.8.2 | Construction Requirements - Hose Assemblies | Yes | Mandatory | The hose and coupling or crimping system shall function throughout the operating temperature range, and coupling systems shall be designed and fitted in such a way that they cannot damage the hose. | Satisfactory / Unsatisfactory (The hose and coupling or crimping system is not function throughout the operating temperature range, and coupling systems is not designed and not fitted in such a way that they can damage the hose) | Type, Class | Clause 9.8.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.8.3 | Construction Requirements - Hose Assemblies | Yes | Mandatory | The burst pressure of a hose assembly fitted with a shut-off nozzle shall be equal to or greater. | Satisfactory / Unsatisfactory (The burst pressure of a hose assembly fitted with a shut-off nozzle is not equal to or greater) | Type, Class | Clause 9.8.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.8.3 | Construction Requirements - Hose Assemblies | Yes | Mandatory | The test pressureis not established by increasing the pressure to the minimum allowable burst pressure in a time no less than 30 s, not maintaining that pressure for 30 s during which failure occurred and then increasing the pressure until failure occurred. | Satisfactory / Unsatisfactory (The burst pressure of a hose assembly fitted with a shut-off nozzle is not equal to or greater) | Type, Class | Clause 9.8.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.8.4 | Construction Requirements - Hose Assemblies | Yes | Mandatory | A hose assembly without a shut-off nozzle shall be capable of withstanding, without leakage, a hydrostatic pressure equal to the extinguisher test pressure, (Pt ) held for at least 30 s. | Satisfactory / Unsatisfactory (A hose assembly without a shut-off nozzle is not capable of withstanding, without leakage, a hydrostatic pressure equal to the extinguisher test pressure, (Pt ) not held for at least 30 s) | Type, Class | Clause 9.8.4 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.9.1 | Method of Operation (Batch Test) | Yes | Mandatory | The forces or the energy necessary to operate the extinguisher shall not exceed the values given in Table 10 for temperatures up to 55 °C. | Satisfactory / Unsatisfactory (The forces or the energy necessary to operate the extinguisher is having exceeded the values) | Type, Class | Clause 9.9.1 | IS 15683 | 4
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical |  | Clause 9.9.1, Table 10 | Force or Energy Required to Operate the Extinguisher | Yes | Mandatory | Force required to operate extinguisher with one finger, N, Max | Value to be specified in integers or whole numbers | Type, Class |  |  | 1 | 100 | 100 | 100 |  |  | 100 |  | 100 |  | 100 |  | 100 |  | 100
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical |  | Clause 9.9.1, Table 10 | Force or Energy Required to Operate the Extinguisher | Yes | Mandatory | Force required to operate extinguisher with full hand, N, Max | Value to be specified in integers or whole numbers | Type, Class |  |  | 2 | 200 | 300 | 200 |  |  | 200 |  | 300 |  | 200 |  | 200 |  | 200
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical |  | Clause 9.9.1, Table 10 | Force or Energy Required to Operate the Extinguisher | Yes | Mandatory | Energy Required to Operate the Extinguisher With impact (strike knob), J | Value to be specified in integers or whole numbers | Type, Class |  |  | 3 |  |  |  | Maximum or minimum requirement is not mentioned in the standards |  | 2 |  | 2 |  | 2 |  | 2 |  | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.10.1 | Safety-Locking Devices (Batch Test) | Yes | Mandatory | The operating mechanism shall be provided with a safety device to prevent inadvertent operation. | Satisfactory / Unsatisfactory (The operating mechanism is not provided with a safety device to prevent inadvertent operation) | Type, Class | Clause 9.10.1 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.10.1 | Safety-Locking Devices (Batch Test) | Yes | Mandatory | The release of the safety device with tamper indicator shall involve an operation distinct from that of the operation mechanism | Satisfactory / Unsatisfactory (Operation is not distinct) | Type, Class | Clause 9.10.1 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.10.1 | Force | Yes | Mandatory | Force requires to release of the safety device, N | Value to be specified in integers or whole numbers | Type, Class | Clause 9.10.1 | IS 15683 | 3 |  |  |  |  | 20 | 100 | 20 | 100 | 20 | 100 | 20 | 100 | 20 | 100
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.10.1 | Safety-Locking Devices (Batch Test) | Yes | Mandatory | It shall be possible to determine whether the apparatus may have been operated. | Satisfactory / Unsatisfactory (It is not able to determine whether the apparatus may have been operated) | Type, Class | Clause 9.10.1 | IS 15683 | 4
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.10.2 | Safety-Locking Devices (Batch Test) | Yes | Mandatory | The safety-locking device shall be made of a corrosion resistant material. | Satisfactory / Unsatisfactory (non corrosion resistant material) | Type, Class | Clause 9.10.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.10.3 | Safety-Locking Devices (Batch Test) | Yes | Mandatory | The safety-locking pin or other device shall be visible from the front of the extinguisher when the extinguisher is mounted in its mounting bracket. EXCEPTION — The safety-locking pin may be on the reverse side of the extinguisher if pictographic operating instructions on the front illustrate the intended method of operation | Satisfactory / Unsatisfactory ( The safety-locking pin or other device is not visible from the front of the extinguisher when the extinguisher is mounted in its mounting bracket) | Type, Class, Mounting | Clause 9.10.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.10.4 | Safety-Locking Devices (Batch Test) | Yes | Mandatory | If the safety-locking device is attached to the extinguisher by a chain or similar device, the chain shall be attached so as to not interfere with the discharge stream. | Satisfactory / Unsatisfactory (If the safety-locking device is not attached to the extinguisher by a chain or similar device, the chain is not attached so as interfere with the discharge stream) | Type, Class | Clause 9.10.4 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | Clause 9.10.5 | Safety-Locking Devices (Batch Test) | Yes | Mandatory | A tamper indicator such as a seal shall be provided to retain the safety-locking device in place and to indicate tampering with or use of the extinguisher. | Satisfactory / Unsatisfactory (A tamper indicator such as a seal is not provided to retain the safety-locking device in place and to indicate tampering with or use of the extinguisher) | Type, Class | Clause 9.10.5 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.10.6 | Safety-Locking Devices (Batch Test) | Yes | Mandatory | The tamper indicator shall be constructed so that it must be broken to operate the extinguisher. | Satisfactory / Unsatisfactory (The tamper indicator is not constructed so that it is not broken to operate the extinguisher) | Type, Class | Clause 9.10.6 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Quantitative | Clause 9.10.6 | Safety-Locking Devices (Batch Test) | Yes | Mandatory | the force required to accomplish discharge or release of the internal load | Value to be specified in integers or whole numbers | Type, Class | Clause 9.10.6 | IS 15683 | 2 |  |  |  |  | 70 | 100 | 70 | 100 | 70 | 100 | 70 | 100 | 70 | 100
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.1 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | A rechargeable extinguisher of the storedpressure type (except carbon dioxide) employing a single chamber for both the extinguishing medium and the expellant gas shall be equipped with a pressure gauge to show the amount of pressure in the chamber regardless if the valve is opened or closed. | Satisfactory / Unsatisfactory (A rechargeable extinguisher of the storedpressure type (except carbon dioxide) not employing a single chamber for both the extinguishing medium and the expellant gas is not equipped with a pressure gauge to show the amount of pressure in the chamber regardless if the valve is opened or closed) | Type, Class | 9.11.1.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.2 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | The operable pressure range of the gauge shall reflect preferably the operating temperature-pressure relationship of the extinguisher (see 7.1). | Satisfactory / Unsatisfactory (The operable pressure range of the gauge is not reflect the operating temperature-pressure relationship of the extinguisher). | Type, Class | 9.11.1.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.3 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | The pressure gauge face shall indicate the appropriate units for which the gauge is calibrated, such as bar, or kPa, or any other of pressure units. | Satisfactory / Unsatisfactory (The pressure gauge face is not indicated the appropriate units for which the gauge is calibrated, such as bar, or kPa, or any other of pressure units) | Type, Class | 9.11.1.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.4 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | The minimum indicated range of the pressure in the gauge shall be 0 to 20 bar. | Satisfactory / Unsatisfactory (The minimum indicated range of the pressure in the gauge is not indicated 0 to 20 bar) | Type, Class | 9.11.1.4 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.4 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | The gauge dial shall indicate, in green, the operable pressure range of the extinguisher. | Satisfactory / Unsatisfactory (The gauge dial is not indicated, in green, the operable pressure range of the extinguisher) | Type, Class | 9.11.1.4 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.4 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | The zero, service, and maximum indicated gauge pressures shall be shown with suitable marks. | Satisfactory / Unsatisfactory (The zero, service, and maximum indicated gauge pressures is not showing with suitable marks) | Type, Class | 9.11.1.4 | IS 15683 | 3
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.4 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | The arc of the dial from the zero pressure point to the lower end of the operable range shall read ‘Recharge’ or suitably marked. | Satisfactory / Unsatisfactory (The arc of the dial from the zero pressure point to the lower end of the operable range is not readable as ‘Recharge’ or suitably marked) | Type, Class | 9.11.1.4 | IS 15683 | 4
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.4 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | The arc of the dial from the higher end of the operable range to the maximum indicated pressure shall read ‘Overcharged’ or suitably marked. | Satisfactory / Unsatisfactory (The arc of the dial from the higher end of the operable range to the maximum indicated pressure is not readable as ‘Overcharged’ or suitably marked) | Type, Class | 9.11.1.4 | IS 15683 | 5
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.4 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | The area of service pressure range shall be marked with suitable colour. | Satisfactory / Unsatisfactory (The area of service pressure range is not marked with suitable colour) | Type, Class | 9.11.1.4 | IS 15683 | 6
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.4 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | All numerals, letters, and characters in the recharge, operable, and overcharge portions of the dial shall be marked with any distinguished colour. | Satisfactory / Unsatisfactory (All numerals, letters, and characters in the recharge, operable, and overcharge portions of the dial is not marked with any distinguished colour) | Type, Class | 9.11.1.4 | IS 15683 | 7
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.1.4 | Requirements for Pressure Gauges and Indicators for Low-Pressure Extinguishers - General | Yes | Mandatory | Pointers shall be of prominent colour preferably contrast to the base colour, and the tip of the pointer shall end in the arc. | Satisfactory / Unsatisfactory (Pointers is not of prominent colour preferably contrast to the base colour, and the tip of the pointer is not end in the arc) | Type, Class | 9.11.1.4 | IS 15683 | 8
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.2 | Calibration/Checking/Verification Test for Pressure Gauges and Indicators | Yes | Mandatory | The error of a pressure gauge at the indicated service pressure (Ps) shall not exceed ± 4 percent of the service pressure. | Satisfactory / Unsatisfactory (The error of a pressure gauge at the indicated service pressure (Ps) has exceeded ± 4 percent of the service pressure) | Type, Class | 9.11.2 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.2 | Calibration/Checking/Verification Test for Pressure Gauges and Indicators | Yes | Mandatory | The error at the upper and lower limits of the operable range shall not exceed ± 4 percent of the service pressure for powder and water-based extinguisher gauges and ± 8 percent of the charging pressure for clean agent extinguisher gauges. | Satisfactory / Unsatisfactory (The error at the upper and lower limits of the operable range is having exceeded ± 4 percent of the service pressure for powder and water-based extinguisher gauges and ± 8 percent of the charging pressure for clean agent extinguisher gauges) | Type, Class | 9.11.2 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.2 | Calibration/Checking/Verification Test for Pressure Gauges and Indicators | Yes | Mandatory | At the zero-pressure mark, the error shall not exceed - 0 percent to + 12 percent of the service pressure (Ps). | Satisfactory / Unsatisfactory (At the zero-pressure mark, the error is having exceeded - 0 percent to + 12 percent of the service pressure (Ps)) | Type, Class | 9.11.2 | IS 15683 | 3
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.2 | Calibration/Checking/Verification Test for Pressure Gauges and Indicators | Yes | Mandatory | At the maximum indicated pressure, the error shall not exceed ± 15 percent of the service pressure (Ps). | Satisfactory / Unsatisfactory (At the maximum indicated pressure, the error is having exceeded ± 15 percent of the service pressure (Ps)) | Type, Class | 9.11.2 | IS 15683 | 4
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.3.1 | Burst Strength Test — Gauges and Indicators | Yes | Mandatory | A pressure gauge or an indicator shall withstand, for 1 min, a pressure of minimum 25 kg/cm2 without rupture. | Satisfactory / Unsatisfactory (A pressure gauge or an indicator is not withstand, for 1 min, a pressure of minimum 25 kg/cm2 without rupture) | Type, Class | 9.11.3.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.11.4 | Water Resistance Test — Gauges and Indicators | Yes | Mandatory | A gauge or indicator for use on an extinguisher shall remain watertight after being immersed at a depth of 0.3 m in water for 2 h, and after being subjected to the salt-spray corrosion test (see 7.6.1). | Satisfactory / Unsatisfactory (A gauge or indicator for use on an extinguisher is not having watertight after being immersed at a depth of 0.3 m in water for 2 h, and after being subjected to the salt-spray corrosion test) | Type, Class | 9.11.4 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.12.1 | Dip-Tubes and Filters — Water-Based Extinguishers | Yes | Mandatory | The dip-tube and filter of water-based extinguishers shall be constructed of materials resistant to the extinguishing medium (see 9.7.3). | Satisfactory / Unsatisfactory (The dip-tube and filter of water-based extinguishers is not constructed of materials resistant to the extinguishing medium) | Type, Class | 9.12.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 9.13 | Horn Test for Carbon Dioxide (CO2) Extinguishers (Type Test) | Yes | Mandatory | The extinguisher horn shall withstand crushing when 25 kg is applied to its extremity for 5 min immediately after having completely discharged the extinguisher through the horn. | Satisfactory / Unsatisfactory (The extinguisher horn is not withstand crushing when 25 kg is applied to its extremity for 5 min immediately after having completely discharged the extinguisher through the horn) | Type, Class | 9.13 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | 9.14.1 | Requirements for Extinguishants Filled in the Extinguisher | Yes | Mandatory | For ABC powder type extinguisher, the content of mono ammonium phosphate shall not be less than 40 percent when tested as per method given in IS 4308. | Please see the Test Report of IS 4308 |  |  | IS 4308 |  |  |  |  | The Treq and Trep formats of referred IS 4308 is required to be prepared separatelly in future
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | 9.14.2 | Requirements for Extinguishants Filled in the Extinguisher | Yes | Mandatory | For BC powder type extinguisher, the content of sodium bicarbonate/potassium bicarbonate shall not be less than 75 percent when tested as per method given in IS 4308. | Please see the Test Report of IS 4308 |  |  | IS 4308 |  |  |  |  | The Treq and Trep formats of referred IS 4308 is required to be prepared separatelly in future
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Chemical | Quantitative | 9.14.3 | Requirements for Extinguishants Filled in the Extinguisher | Yes | Mandatory | For foam type extinguisher, the surface tension shall not be more than 18 dyne/cm when tested as per the method given in IS 4989. | Please see the Test Report of IS 4989 |  |  | IS 4989 |  |  |  |  | The Treq and Trep formats of referred IS 4989 is required to be prepared separatelly in future
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.1 | Marking and Colour | Yes | Mandatory | The recommended colour for extinguisher bodies is red conforming to shade No. 536 or 538 of IS 5 |  |  |  | IS 5 | 1 |  |  |  |  | Red | Red | Black | Black | Green | Green | Blue | Blue | Yellow | Yellow
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.1 | Marking and Colour | Yes | Mandatory | A small band of distinguishing colour of approx 5 percent/prominent of surface area shall be painted or labelled (as per IS 17917) for different type of extinguishers. | Satisfactory / Unsatisfactory (A small band of distinguishing colour of approx 5 percent/prominent of surface area is not painted or labelled (as per IS 17917) for different type of extinguishers) | Class, Type, Size, Material | 10.1 | IS 15683 | 2 |  |  |  | The Treq and Trep formats of referred IS 17917 is required to be prepared separatelly in future
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.1 | Marking | Yes | Mandatory | The operating, recharging, and inspection and maintenance instructions shall be in the form of an etched or embossed metal nameplate or band, or an acceptable pressure-sensitive nameplate attached to the side of the extinguisher body, or in the form of silk-screening of paint directly on the extinguisher body or in the form of label. | Satisfactory / Unsatisfactory (The operating, recharging, and inspection and maintenance instructions are not in the form of an etched or embossed metal nameplate or band, or an acceptable pressure-sensitive nameplate attached to the side of the extinguisher body, or in the form of silk-screening of paint directly on the extinguisher body or in the form of label) | Class, Type, Size, Material | 10.2.1.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.2 | Marking | Yes | Mandatory | The marking shall include a sequential serial number. | Satisfactory/ Unsatisfactory (The marking is not included a sequential serial number) | Class, Type, Size, Material | 10.2.1.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.3 | Marking | Yes | Mandatory | The year of manufacture, or the last two digits of the calendar year, and the factory test pressure shall be permanently marked into the extinguisher body or non-transferable nameplate. | Satisfactory/ Unsatisfactory (The year of manufacture, or the last two digits of the calendar year, and the factory test pressure is not marked into the extinguisher body or non-transferable nameplate) | Class, Type, Size, Material | 10.2.1.3 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.3 | Marking | Yes | Mandatory | Extinguishers manufactured in the last three months of a calendar year may be marked with the following year as the date of manufacture, and extinguishers manufactured in the first three months of a calendar year may be marked with the previous year as the date of manufacture. | Satisfactory/ Unsatisfactory (Extinguishers manufactured in the last three months of a calendar year may be marked with the following year as the date of manufacture, and extinguishers manufactured in the first three months of a calendar year may be marked with the previous year as the date of manufacture) | Class, Type, Size, Material | 10.2.1.2 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.4 | Marking | Yes | Mandatory | The marking shall include a reference to the range of temperatures at which the extinguisher is usable, such as ‘Acceptable to use at temperature from …°C to …°C’ or the equivalent. | Satisfactory/ Unsatisfactory (The marking is not included a reference to the range of temperatures at which the extinguisher is usable, such as ‘Acceptable to use at temperature from …°C to …°C’ or the equivalent) | Class, Type, Size, Material | 10.2.1.4 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.5 | Marking | Yes | Mandatory | The following applicable statement or the equivalent shall be included in the marking: a) For rechargeable extinguishers: ‘Recharge immediately after any use’; and | Satisfactory/ Unsatisfactory ("Recharged immediately after any use" is not provided for marking) | Class, Type, Size, Material | 10.2.1.5 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.5 | Marking | Yes | Mandatory | The following applicable statement or the equivalent shall be included in the marking: b) For disposable extinguishers: ‘Discard immediately after any use’. | Satisfactory/ Unsatisfactory ("Discard immediately after any use" is not provided for marking) | Class, Type, Size, Material | 10.2.1.5 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.6 | Marking | Yes | Mandatory | The gas cartridge shall be permanently marked with the following: a) Empty mass, in g; | Satisfactory/ Unsatisfactory (Empty mass not provided) | Class, Type, Size, Material | 10.2.1.6 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.6 | Marking | Yes | Mandatory | The gas cartridge shall be permanently marked with the following: b) Nominal full mass, in g | Satisfactory/ Unsatisfactory ("Nominal full mass" is not provided for marking) | Class, Type, Size, Material | 10.2.1.6 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.6 | Marking | Yes | Mandatory | The gas cartridge shall be permanently marked with the following: c) Year of manufacture | Satisfactory/ Unsatisfactory ("year of manufacture" is not provided for marking) | Class, Type, Size, Material | 10.2.1.6 | IS 15683 | 3
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.6 | Marking | Yes | Mandatory | The gas cartridge shall be permanently marked with the following: d) Name or code of the manufacturer | Satisfactory/ Unsatisfactory ("Name or code of the manufacturer" is not marked) | Class, Type, Size, Material | 10.2.1.6 | IS 15683 | 4
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.6 | Marking | Yes | Mandatory | If the cartridge is mounted on the outside of the extinguisher media chamber, information may be placed on the cartridge in the form of a decalcomania transfer | Satisfactory/ Unsatisfactory (If the cartridge is mounted on the outside of the extinguisher media chamber, information is not placed on the cartridge in the form of a decalcomania transfer, if not applicable) | Class, Type, Size, Material | 10.2.1.6 | IS 15683 | 5
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.6 | Marking | Yes | Mandatory | If the cartridge is mounted inside the media chamber, this information shall be stenciled or stamped on the cartridge. | Satisfactory/ Unsatisfactory (If the cartridge is mounted inside the media chamber, this information is not stenciled or stamped on the cartridge) | Class, Type, Size, Material | 10.2.1.6 | IS 15683 | 6
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.7 | Marking | Yes | Mandatory | The marking on each extinguisher shall include its exact gross mass or minimum and maximum gross mass, which may be expressed by a tolerance | Satisfactory/ Unsatisfactory (The marking on each extinguisher is not included its exact gross mass or minimum and maximum gross mass, which may be expressed by a tolerance) | Class, Type, Size, Material | 10.2.1.7 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.7 | Marking | Yes | Mandatory | The gross mass shall include the mass of the charged extinguisher and discharge assembly | Satisfactory/ Unsatisfactory (The gross mass is not included the mass of the charged extinguisher and discharge assembly) | Class, Type, Size, Material | 10.2.1.7 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.8 | Marking | Yes | Mandatory | The chemical name of the clean agent shall be marked on the label of the clean agent extinguisher. | Satisfactory/ Unsatisfactory (The chemical name of the clean agent is not marked on the label of the clean agent extinguisher) | Class, Type, Size, Material | 10.2.1.8 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.9 | BIS certification marking | Yes | Mandatory | The extinguisher may also be marked with the Standard Mark. | Satisfactory/ Unsatisfactory (The extinguisher is not marked with the Standard Mark, if not applicable) | Class, Type, Size, Material | 10.2.1.9 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.1.9.1 | BIS certification marking | Yes | Mandatory | The use of the Standard Mark is governed by the provisions of the Bureau of Indian Standards Act, 2016 and the Rules and Regulations made thereunder. The details of the conditions under which the licence for use of the Standard Mark may be granted to manufacturers or producers may be obtained from the Bureau of Indian Standards | Satisfactory/ Unsatisfactory (The use of the Standard Mark is not governed by the provisions of the Bureau of Indian Standards Act, 2016 and the Rules and Regulations made thereunder. The details of the conditions under which the licence for use of the Standard Mark is not granted to manufacturers or producers is not obtained from the Bureau of Indian Standards, if not applicable) | Class, Type, Size, Material | 10.2.1.9.1 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2 | Operating Instructions | Yes | Mandatory | For the purpose of applying the requirements of this section, the ‘operating instructions’ are defined as those necessary to accomplish intended discharge of the extinguishing media including any warnings. An example of the layout marking is given in Fig. 7. | Satisfactory/ Unsatisfactory (Clean-agent fire extinguishers is not contained the following warning or equivalent as part of the operating instructions: WARNING — The concentrated agent when applied to the fire can produce toxic by-products. Avoid inhalation of these materials by evacuating and ventilating the area) | Class, Type, Size, Material | 10.2.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2.2 | Marking | Yes | Mandatory | Clean-agent fire extinguishers shall contain the following warning or equivalent as part of the operating instructions: WARNING — The concentrated agent when applied to the fire can produce toxic by-products. Avoid inhalation of these materials by evacuating and ventilating the area. | Satisfactory/ Unsatisfactory (Clean-agent fire extinguishers shall contain the following warning or equivalent as part of the operating instructions: WARNING — The concentrated agent when applied to the fire can produce toxic by-products. Avoid inhalation of these materials by evacuating and ventilating the area. | Class, Type, Size, Material | 10.2.2.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2.3 | Marking | Yes | Mandatory | The operating instructions shall face outward and cover no more than a 120° arc on the extinguisher body. The marking required in 10.2.2.4 and 10.2.3 shall together occupy a minimum surface area of 75 cm2 for an extinguisher having a diameter greater than 80 mm and 50 cm2 for and extinguisher having a diameter of 80 mm or less. | Satisfactory/ Unsatisfactory (The operating instructions is not face outward and cover no more than a 120° arc on the extinguisher body. The marking required in 10.2.2.4 and 10.2.3 are not together occupied a minimum surface area of 75 cm2 for an extinguisher not having a diameter greater than 80 mm and 50 cm2 for and extinguisher not having a diameter of 80 mm or less. | Class, Type, Size, Material | 10.2.2.3 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2.4 | Marking | Yes | Mandatory | The operating instructions shall be arranged as follows: a) Word ‘INSTRUCTIONS’ shall be at the top of the nameplate. The minimum letter height shall be 6.0 mm for an extinguisher having a diameter greater than 80.0 mm and 5.0 mm for an extinguisher having a diameter of 80.0 mm or less. As an option, the words FIRE EXTINGUISHER or EXTINGUISHER may be added to the word INSTRUCTIONS; | Satisfactory/ Unsatisfactory (Word ‘INSTRUCTIONS’ is not given at the top of the nameplate. The minimum letter height is not having 6.0 mm for an extinguisher not having a diameter greater than 80.0 mm and 5.0 mm for an extinguisher not having a diameter of 80.0 mm or less. As an option, the words FIRE EXTINGUISHER or EXTINGUISHER is not added to the word INSTRUCTIONS, if applicable) | Class, Type, Size, Material | 10.2.2.4 | IS 15683 | 1
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2.4 | Marking | Yes | Mandatory | The operating instructions shall be arranged as follows: b) Operating instructions shall be in the form of numerically sequenced pictographs. A single pictograph may include two instructions; | Satisfactory/ Unsatisfactory (Operating instructions is not in the form of numerically sequenced pictographs. A single pictograph is not included two instructions, if applicable) | Class, Type, Size, Material | 10.2.2.4 | IS 15683 | 2
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2.4 | Marking | Yes | Mandatory | The operating instructions shall be arranged as follows: Sequence of pictographs shall illustrate, with pictures, the recommended actions necessary for intended operation of the extinguisher. Words may be added. | Satisfactory/ Unsatisfactory (Sequence of pictographs is not illustrated, with pictures, the recommended actions necessary for intended operation of the extinguisher. Words is not added, if applicable) | Class, Type, Size, Material | 10.2.2.4 | IS 15683 | 3
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2.4 | Marking | Yes | Mandatory | The sequence shall be as follows: 1) Making ready the extinguisher by disengaging the safety-locking device; | Satisfactory/ Unsatisfactory (not making ready the extinguisher by disengaging the safety-locking device) | Class, Type, Size, Material | 10.2.2.4 | IS 15683 | 4
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2.4 | Marking | Yes | Mandatory | The sequence shall be as follows: 2) Aiming the extinguisher at the base of the fire, including the recommended distance from the fire at which to begin discharge, and indicating the intended operating attitude of the extinguisher; | Satisfactory/ Unsatisfactory (Not aiming the extinguisher at the base of the fire, including the recommended distance from the fire at which to begin discharge, and not indicating the intended operating attitude of the extinguisher; | Class, Type, Size, Material | 10.2.2.4 | IS 15683 | 5
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2.4 | Marking | Yes | Mandatory | The sequence shall be as follows: 3) Taking whatever action necessary to initiate operation of the extinguisher; and | Satisfactory/ Unsatisfactory (not taking whatever action necessary to initiate operation of the extinguisher) | Class, Type, Size, Material | 10.2.2.4 | IS 15683 | 6
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2.4 | Marking | Yes | Mandatory | The sequence shall be as follows: 4) Describing the intended method of applying the extinguishing media on the fire | Satisfactory/ Unsatisfactory (not describing the intended method of applying the extinguishing media on the fire) | Class, Type, Size, Material | 10.2.2.4 | IS 15683 | 7
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.2.5 | Marking | Yes | Mandatory | The extinguisher shall be marked with letters ‘A’, ‘B’ and ‘C’ indicating their suitability for respective class of fires as laid down in IS 2190, and numerical indicating size of fire such 2A and 21B, etc. | Satisfactory/ Unsatisfactory (The extinguisher is not marked with letters ‘A’, ‘B’ and ‘C’ indicating their suitability for respective class of fires as laid down in IS 2190, and numerical indicating size of fire such 2A and 21B, etc) | Class, Type, Size, Material | 10.2.2.5 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.3.1 | Marking | Yes | Mandatory | Use code symbols (see Fig. 8) shall be positioned directly below the operating instructions. A written description for each use code symbol may be included as part of the code. The description should be readable. | Satisfactory/ Unsatisfactory (Use code symbols is not positioned directly below the operating instructions. A written description for each use code symbol not included as part of the code, if applicable. The description is not showing as "readable") | Class, Type, Size, Material | 10.2.3.1 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.3.2 | Marking | Yes | Mandatory | Use code symbols shall be placed on the extinguisher for those types of fires for which the extinguisher is classified. | Satisfactory/ Unsatisfactory (Use code symbols is not placed on the extinguisher for those types of fires for which the extinguisher is classified) | Class, Type, Size, Material | 10.2.3.2 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 10.2.4 | Marking | Yes | Mandatory | The recharging instructions on the marking of a rechargeable extinguisher shall state the intended mass and agent that shall be used in recharging, the intended expellant gas pressure or the use of a correct and a fully charged gas cartridge. Reference shall be made to use only the manufacturer’s replacement parts in recharging the extinguisher. However, in lieu of detailed recharge instructions, these instructions may simply instruct the user to return the extinguisher to the dealer or manufacturer for recharging, using the following words or the equivalent: ‘Return to an authorized recharger for recharging in accordance with Service Manual No…’. It is mandatory to recharge the extinguisher by manufacturer or authorized agent of manufacturer. | Satisfactory/ Unsatisfactory (not used in recharging, the intended expellant gas pressure or the use of a correct and a fully charged gas cartridge) | Class, Type, Size, Material | 10.2.2.4 | IS 15683
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 11.1 | Manuals | No | Mandatory | A user manual shall be provided with each extinguisher | Satisfactory/ Unsatisfactory (A user manual is not provided with each extinguisher) | Class, Type, Size, Material | 11.1 | IS 15683 | 1 |  |  |  | To be verified by IO officer
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 11.1 | Manuals | No | Mandatory | This manual shall contain the necessary instructions, warnings, and cautions for the intended installation, operation and inspection of the extinguisher | Satisfactory/ Unsatisfactory (This manual not containing the necessary instructions, warnings, and cautions for the intended installation, operation and inspection of the extinguisher) | Class, Type, Size, Material | 11.1 | IS 15683 | 2 |  |  |  | To be verified by IO officer
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 11.1 | Manuals | No | Mandatory | The manual shall also refer the manufacturer’s service manual for maintenance and recharging of the extinguisher | Satisfactory/ Unsatisfactory (The manual is not referred the manufacturer’s service manual for maintenance and recharging of the extinguisher) | Class, Type, Size, Material | 11.1 | IS 15683 | 3 |  |  |  | To be verified by IO officer
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 11.1 | Manuals | No | Mandatory | The manufacturer shall prepare a service manual for each model fire extinguisher. It shall be made available upon request and shall, a) contain necessary instruction, warnings, and cautions, a description of servicing equipment, and a description of recommended operations for intended servicing; | Satisfactory/ Unsatisfactory (not contained necessary instruction, warnings, and cautions, a description of servicing equipment, and a description of recommended operations for intended servicing) | Class, Type, Size, Material | 11.1 | IS 15683 | 4 |  |  |  | To be verified by IO officer
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 11.1 | Manuals | No | Mandatory | The manufacturer shall prepare a service manual for each model fire extinguisher. It shall be made available upon request and shall, b) provide a list of part numbers of all replaceable parts; and | Satisfactory/ Unsatisfactory (not provided a list of part numbers of all replaceable parts) | Class, Type, Size, Material | 11.1 | IS 15683 | 5 |  |  |  | To be verified by IO officer
15683 | 0 | 0 | 2018 | 1 | Portable Fire extinguishers - Performance and Construction | Mechanical | Qualitative | 11.1 | Manuals | No | Mandatory | The manufacturer shall prepare a service manual for each model fire extinguisher. It shall be made available upon request and shall, c) indicate that the pressure gauge attached to the extinguisher shall not be used to determine when the intended service pressure has been reached, and a pressure regulator shall be used if the pressure service is a tank of high pressure gas. | Satisfactory/ Unsatisfactory (the pressure gauge attached to the extinguisher is not used to determine when the intended service pressure has been reached, and a pressure regulator is not used if the pressure service is a tank of high pressure gas. | Class, Type, Size, Material | 11.1 | IS 15683 | 6 |  |  |  | To be verified by IO officer

## TReq - Review
IS 15683 |  | Test Request Format
Extinguisher media | Propellants | Nominal charge capacity (ltr.) | Nominal charge capacity (kg) | Class | Extinguisher type based on pressure | Extinguisher type based on Mounting | Operating temperature | Type of Cylinder body
Water based | Air | 2 | 1 | Class - 1A | High Pressure | wall mounting | +5°C to + 60°C | Steel
Foam based | Carbondioxide | 3 | 2 | Class - 2A | Low Pressure | non wall mounting | 0°C to + 60°C | Aluminium
Powder based extinguisher (AB,BC,D Type) | Nitrogen | 4 | 3 | Class - 3A |  |  | − 10°C to + 60°C | Low carbon steel
Carbon dioxide based |  | 6 | 4 | Class - 4A |  |  | − 20°C to + 60°C | stainless steel
Clean agent |  | 9 | 5 | Class - 6A |  |  | − 30°C to + 60°C | Composite
Water mist type |  | - | 6 | Class - 10A |  |  | - | -
- |  | - | 9 | Class - 15A |  |  | - | -
- |  | - | 12 | Class - 20A |  |  | - | -
Class - 8B
Class - 13B
Class - 21B
Class - 34B
Class - 55B
Class - 70B
Class - 89B
Class - 113B
Class - 144B
Class - 183B
Class - 233B
Class C
Class D
Class F