## IS 60898_1_0_2015_0_Test Report
IS Number | Part | Section | Year | Number of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause/ Table/ Annex Reference | Test Parameter Name | To be tested and/or reported by Lab (Yes/No)” | Mandatory or Optional | Characteristics (As per Indian Standard) | Test Result/ Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference | Sample Quantity | Equipment | Remarks | Type B, In<=63 A Min | Type B, In<=63 A Max | Type B, In>63 A Min | Type B, In>63 A Max | Type B, In<=32 A Min | Type B, In<=32 A Max | Type B, In>32 A Min | Type B, In>32 A Max | Type C, In<=63 A Min | Type C, In<=63 A Max | Type C, In>63 A Min | Type C, In>63 A Max | Type C, In<=32 A Min | Type C, In<=32 A Max | Type C, In>32 A Min | Type C, In>32 A Max | Type D, In<=63 A Min | Type D, In<=63 A Max | Type D, In>63 A Min | Type D, In>63 A Max | Type D, In<=32 A Min | Type D, In<=32 A Max | Type D, In>32 A Min | Type D, In>32 A Max | circuit-breakers with flat quick-connect terminals for external copper conductors, Min | circuit-breakers with flat quick-connect terminals for external copper conductors, Max | circuit-breakers with screw-type terminals for external aluminium conductors Min | circuit-breakers with screw-type terminals for external aluminium conductors Max | In ≤10 Min | In ≤10 Max | 10< In ≤ 16 Min | 10< In ≤ 16 Max | 16< In ≤ 25 Min | 16< In ≤ 25 Max | 25< In ≤ 32 Min | 25< In ≤ 32 Max | 32< In ≤ 40 Min | 32< In ≤ 40 Max | 40< In ≤ 50 Min | 40< In ≤ 50 Max | 50< In ≤ 63 Min | 50< In ≤ 63 Max | 63< In ≤ 100 Min | 63< In ≤ 100 Max | 100< In ≤ 125 Min | 100< In ≤ 125 Max | Uimp - 2,5 kV, 120/240, 120 MIN | Uimp - 2,5 kV, 120/240, 120 MAX | Uimp - 4 kV, 120/240 240 MIN | Uimp - 4 kV, 120/240, 240 MAX | Uimp - 4 kV, 230/400 230 400 MIN | Uimp - 4 kV, 230/400 230 400 MAX | Material Group IIIa, >25 <=50 MIN | Material Group IIIa, >25 <=50 MAX | Material Group IIIa, 120 MIN | Material Group IIIa, 120 MAX | Material Group IIIa, 250 MIN | Material Group IIIa, 250 MAX | Material Group IIIa, 400 MIN | Material Group IIIa, 400 MAX | Material Group IIa, >25 <=50 MIN | Material Group IIa, >25 <=50 MAX | Material Group IIa, 120 MIN | Material Group IIa, 120 MAX | Material Group IIa, 250 MIN | Material Group IIa, 250 MAX | Material Group IIa, 400 MIN | Material Group IIa, 400 MAX | Material Group I, >25 <=50 MIN | Material Group I, >25 <=50 MAX | Material Group I, 120 MIN | Material Group I, 120 MAX | Material Group I, 250 MIN | Material Group I, 250 MAX | Material Group I, 400 MIN | Material Group I, 400 MAX | Material Group IIIa, Rated Voltage 120/240 V Min | Material Group IIIa, Rated Voltage 120/240 V Max | Material Group IIIa, Rated Voltage 230/400 V Min | Material Group IIIa, Rated Voltage 230/400 V Max | Material Group II, Rated Voltage 120/240 V Min | Material Group II, Rated Voltage 120/240 V Max | Material Group II, Rated Voltage 230/400 V Min | Material Group II, Rated Voltage 230/400 V Max | Material Group I, Rated Voltage 120/240 V Min | Material Group I, Rated Voltage 120/240 V Max | Material Group I, Rated Voltage 230/400 V Min | Material Group I, Rated Voltage 230/400 V Max
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 4.2 | Classification | Yes | Mandatory | According to the number of poles: single-pole circuit-breakers; two-pole-circuit-breakers with one protected pole; two-pole circuit-breakers with two protected poles; three-pole circuit-breakers with three protected poles; four-pole circuit-breakers with three protected poles; four-pole circuit-breakers with four protected poles. | To be checked based on declaration basis | No. of poles | Cl.4.2 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 4.3 | Classification | Yes | Mandatory | According to the protection against external influences: enclosed-type (not requiring an appropriate enclosure); unenclosed-type (for use with an appropriate enclosure). | To be checked based on declaration basis | Type of enclosures | Cl.4.3 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 4.4 | Classification | Yes | Mandatory | According to the method of mounting: surface-type; flush-type; panel board type, also referred to as distribution board type. | To be checked based on declaration basis | Method of mounting | Cl.4.4 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 4.5.1 | Classification | Yes | Mandatory | According to the fixation system: circuit-breakers, the electrical connections of which are not associated with the mecha nical mounting; – circuit-breakers, the electrical connections of which are associated with the mechanical mounting. | To be checked based on declaration basis | Method of fixation system | Cl.4.5.1 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 4.5.2 | Classification | Yes | Mandatory | According to the type of terminals: circuit-breakers with screw-type terminals for external copper conductors; – – – circuit-breakers with screwless type terminals for external copper conductors; circuit-breakers with flat quick-connect terminals for external copper conductors; circuit-breakers with screw-type terminals for external aluminium conductors; | To be checked based on declaration basis | Type of terminals | Cl.4.5.2 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 4.6 | Classification | Yes | Mandatory | According to the instantaneous tripping current (see 3.5.17) – B-type; – C-type; – D-type | To be checked based on declaration basis | Type | Cl.4.6 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 4.7 | Classification | Yes | Mandatory | According to the I2t characteristic In addition to the I2t characteristic provided by the manufacturer, circuit-breakers may be classified according to their I2t characteristic. | To be checked based on declaration basis | I2t characterstics | Cl.4.7 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 5.3.1 | Characteristics of circuit-breakers | Yes | Mandatory | Preferred values of rated voltage, V | Number of decimal places - Value to be specified in Integers | Rated Voltage | Cl.5.3.1 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 5.3.2 | Characteristics of circuit-breakers | Yes | Mandatory | Preferred values of rated current, A | Number of decimal places - Value to be specified in Integers | Rated Current | Cl.5.3.2 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 5.3.3 | Characteristics of circuit-breakers | Yes | Mandatory | Standard values of rated frequency, Hz | Number of decimal places - Value to be specified in Integers | Rated Frequency | Cl.5.3.3 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 5.3.4 | Characteristics of circuit-breakers | Yes | Mandatory | Values of rated short-circuit capacity, A | Number of decimal places - Value to be specified in Integers | Rated short-circuit capacity | Cl.5.3.4 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 5.3.5 | Characteristics of circuit-breakers | Yes | Mandatory | Standard ranges of instantaneous tripping, A | Number of decimal places - Value to be specified in Integers | Rated current, type | Cl.5.3.5 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 5.3.6 | Characteristics of circuit-breakers | Yes | Mandatory | Standard values of rated impulse withstand voltage, V | Number of decimal places - Value to be specified in Integers | Rated Voltage, Phase of the system, Rated impulse withstand voltage | Cl.5.3.6 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:a) manufacturer's name or trade mark | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:b) type designation, catalogue number or serial number; | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:c) rated voltage(s); | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:d) rated current without symbol "A" | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 4 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:e) rated frequency if the circuit-breaker is designed only for one frequency | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 5 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:f) rated short-circuit capacity, in amperes; | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 6 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:g) wiring diagram, unless the correct mode of connection is evident; | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 7 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:h) reference ambient air temperature, if different from 30 °C; | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 8 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:i) degree of protection (only if different from IP20); | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 9 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:j) for type D circuit-breakers: the maximum instantaneous tripping current, if higher than 20 In (see Table 2); | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 10 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:k) rated impulse withstand voltage Uimp if it is 2,5 kV. | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 11 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Each circuit-breaker shall be marked in a durable manner with the following:l) making and breaking capacity on an individual protected pole of multipole circuit breakers (Icn1), if different from Icn. | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 12 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | For circuit-breakers operated by means of two push-buttons, only the push-button designed for the opening operation shall be red and/or be marked with the symbol O (IEC 60417-5008). | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 13 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | If it is necessary to distinguish between the supply and the load terminals, the former shall be indicated by arrows pointing towards the circuit-breaker and the latter by arrows pointing away from the circuit-breaker. | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 14 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Terminals intended exclusively for the neutral shall be indicated by the letter N. | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 15 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6 | Marking and other product information | Yes | Mandatory | Terminals intended for the protective conductor, if any, shall be indicated by the symbol (IEC 60417-5019). | Satisfactory/Unsatisfactory (not marked) |  | 6 | IS/IEC 60898-1 | 16 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 6, 9.3 | Marking and other product information | Yes | Mandatory | Marking shall be indelible and easily legible, and shall not be placed on screws, washers or other removable parts. | Satisfactory/Unsatisfactory (delible or not legible) |  | Cl.9.3 | IS/IEC 60898-1 | 17 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 7.2 | Standard conditions for operation in service - Ambient air temperature range | Yes | Mandatory | Ambient air temperature - The ambient air temperature does not exceed +40 °C; The lower limit of the ambient air temperature is –5 °C; K | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Current (In), No. of Poles | Cl.7.2 | IS/IEC 60898-1 | 1 | N.A | N.A |  | -5 | 40 | -5 | 40 |  |  |  |  | -5 | 40 | -5 | 40 |  |  |  |  | -5 | 40 | -5 | 40
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 7.2 | Standard conditions for operation in service - Ambient air temperature range | Yes | Mandatory | Ambient air temperature - its average over a period of 24 h does not exceed +35 °C.; K, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Current (In), No. of Poles | Cl.7.2 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 35 | - | 35 |  |  |  |  | - | 35 | - | 35 |  |  |  |  | - | 35 | - | 35
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.1 | General | Yes | Mandatory | Circuit-breakers shall be so designed and constructed that, in normal use, their performance is reliable and without danger to the user or surroundings. In general, compliance is checked by carrying out all the relevant tests specified. | Satisfactory or Not Satisfactory (not reliable or danger to the user or surroundings) |  | Cl.8.1.1 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | The moving contacts of all poles of multi pole circuit-breakers shall be so mechanically coupled that all poles, except the switched neutral, if any, make and break substantially together, whether operated manually or automatically, even if an overload occurs on one protected pole only. | Satisfactory or Not Satisfactory (didn't make or break together) |  | Cl..8.1.2 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | The switched neutral pole (see 3:2.7.3) of four-pole circuit-breakers shall not close after and shall not open before the protected poles. | Satisfactory or Not Satisfactory (closed after or opened before the protected poles) |  | Cl..8.1.2 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | If a pole having an appropriate short-circuit making and breaking capacity is used as a neutral pole and the circuit-breaker has an independent manual operation (see 3.4.4), then all poles, including the neutral pole, may operate substantially together. | Satisfactory or Not Satisfactory (didn't operate together) |  | Cl..8.1.2 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test d - For circuit-breakers of the B-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.2 | IS/IEC 60898-1 | 4 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test e - For circuit-breakers of the B-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.2 | IS/IEC 60898-1 | 5 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test d - For circuit-breakers of the C-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.3 | IS/IEC 60898-1 | 6 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test e - For circuit-breakers of the C-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.3 | IS/IEC 60898-1 | 7 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test d - For circuit-breakers of the D-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.4 | IS/IEC 60898-1 | 8 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test e - For circuit-breakers of the D-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.4 | IS/IEC 60898-1 | 9 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | It shall be possible to switch the circuit-breaker on and off by hand. | Satisfactory or Not Satisfactory (not possible to switch the circuit-breaker on and off by hand) | Type of terminals | Cl.8.1.2 | IS/IEC 60898-1 | 10 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | Circuit-breakers shall be so constructed that the moving contacts can come to rest only in the closed position (see 3.2.8) or in the open position (see 3.2.9), even when the operating means is released in an intermediate position. | Satisfactory or Not Satisfactory (can come to rest in position other than closed or opened) |  | Cl.8.1.2 | IS/IEC 60898-1 | 11 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | Circuit-breakers shall provide in the open position (see 3.2.9) an isolation distance in accordance with the requirements necessary to satisfy the isolating function (see 8.3). | Satisfactory or Not Satisfactory (such distance not provided) |  | Cl.8.1.2 | IS/IEC 60898-1 | 12 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | Indication of the open and closed position of the main contacts shall be provided by one or both of the following means: – – the position of the actuator (this being preferred), or a separate mechanical indicator. | Satisfactory or Not Satisfactory (not provided) |  | Cl.8.1.2 | IS/IEC 60898-1 | 13 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | If a separate mechanical indicator is used to indicate the position of the main contacts, this shall show the colour red for the closed position (ON) and the colour green for the open position (OFF). | Satisfactory or Not Satisfactory (not provided) |  | Cl.8.1.2 | IS/IEC 60898-1 | 14 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | The means of indication of the contact position shall be reliable. | Satisfactory or Not Satisfactory (not reliable) |  | Cl.8.1.2 | IS/IEC 60898-1 | 15 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test d - For circuit-breakers of the B-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.2 | IS/IEC 60898-1 | 16 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test e - For circuit-breakers of the B-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.2 | IS/IEC 60898-1 | 17 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test d - For circuit-breakers of the C-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.3 | IS/IEC 60898-1 | 18 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test e - For circuit-breakers of the C-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.3 | IS/IEC 60898-1 | 19 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test d - For circuit-breakers of the D-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.4 | IS/IEC 60898-1 | 20 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Test e - For circuit-breakers of the D-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.4 | IS/IEC 60898-1 | 21 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | Circuit-breakers shall be designed so that the actuator, front plate or cover can only be correctly fitted in a manner which ensures correct indication of the contact position. | Satisfactory or Not Satisfactory (can be fitted incorrectly) |  | Cl.8.1.2 | IS/IEC 60898-1 | 22 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | After the tests according to 9.12.11.2, 9.12.11.3 or 9.12.11.4.2, the circuit-breakers shall show no damage impairing their further use | Satisfactory or Not Satisfactory (damaged impairing further use) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.1 | IS/IEC 60898-1 | 23 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Verification of leakage currents across open contacts (suitability for isolation), leakage current, mA, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.1 | IS/IEC 60898-1 | 24 | N.A | N.A |  | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | Dielectric strength tests according to 9.7.3, carried out between 2 h and 24 h after the short-circuit tests at a voltage of 500 V less than the value prescribed in 9.7.5 and without previous humidity treatment. | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.1 | IS/IEC 60898-1 | 25 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | After the test carried out under the conditions specified in item a) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.1 | IS/IEC 60898-1 | 26 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | After the test carried out under the conditions specified in item b) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.1 | IS/IEC 60898-1 | 27 | N.A | N.A |  | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Moreover, the circuit-breakers shall not trip when a current equal to 0,85 times the conventional non-tripping current is passed through all poles for the conventional time, starting from cold. At the end of this verification the current is steadily increased, within 5 s, to 1,1 times the conventional tripping current. The circuit-breakers shall trip within the conventional time, sec, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.1 | IS/IEC 60898-1 | 28 | N.A | N.A |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | After the tests according to 9.12.11.4.3 and 9.12.11.4.4 the polyethylene foil shall show no holes visible with normal or corrected vision without additional magnification and the circuit breakers shall show no damage impairing their further use | Satisfactory or Not Satisfactory (the polyethylene foil shows holes visible with normal or corrected vision without additional magnification or the circuit breakers shows damage impairing their further use) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.2 | IS/IEC 60898-1 | 29 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Verification of leakage currents across open contacts (suitability for isolation), leakage current, mA, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.5.3 | IS/IEC 60898-1 | 30 | N.A | N.A |  | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | Dielectric strength tests according to 9.7.3, carried out between 2 h and 24 h after the short-circuit tests at a voltage of 900 V and without previous humidity treatment. | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.3 | IS/IEC 60898-1 | 31 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | After the test carried out under the conditions specified in item a) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 a) | IS/IEC 60898-1 | 32 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | After the test carried out under the conditions specified in item b) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 b) | IS/IEC 60898-1 | 33 | N.A | N.A |  | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Moreover the circuit-breakers shall trip within the time corresponding to the test c of Table 7 when a current equal to 2,8 In is passed through all poles, the lower time limit being 0,1 s instead of 1 s, sec, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.2 | IS/IEC 60898-1 | 34 | N.A | N.A | [5 empty] | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | The sample shown as number 1 in Table 23 is not subjected to the verification of this subclause, but it shall nevertheless comply with the requirements of 9.12.10. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.2 | IS/IEC 60898-1 | 35 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | After the tests according to 9.12.11.4.3 and 9.12.11.4.4 the polyethylene foil shall show no holes visible with normal or corrected vision without additional magnification and the circuit breakers shall show no damage impairing their further use | Satisfactory or Not Satisfactory (the polyethylene foil shows holes visible with normal or corrected vision without additional magnification or the circuit breakers shows damage impairing their further use) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.2 | IS/IEC 60898-1 | 36 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Verification of leakage currents across open contacts (suitability for isolation), leakage current, mA, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.5.3 | IS/IEC 60898-1 | 37 | N.A | N.A |  | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | Dielectric strength tests according to 9.7.3, carried out between 2 h and 24 h after the short-circuit tests at a voltage of 900 V and without previous humidity treatment. | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.3 | IS/IEC 60898-1 | 38 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | After the test carried out under the conditions specified in item a) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 a) | IS/IEC 60898-1 | 39 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | After the test carried out under the conditions specified in item b) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 b) | IS/IEC 60898-1 | 40 | N.A | N.A |  | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | - | 5 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.2 | Mechanism | Yes | Mandatory | Moreover the circuit-breakers shall trip within the time corresponding to the test c of Table 7 when a current equal to 2,8 In is passed through all poles, the lower time limit being 0,1 s instead of 1 s, sec, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.2 | IS/IEC 60898-1 | 41 | N.A | N.A | [5 empty] | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | The sample shown as number 1 in Table 23 is not subjected to the verification of this subclause, but it shall nevertheless comply with the requirements of 9.12.10. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.2 | IS/IEC 60898-1 | 42 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | Where the operating means is used to indicate the position of the contacts, the operating means, when released, shall automatically take up the position corresponding to that of the moving contact(s); | Satisfactory or Not Satisfactory (doen't take the position) |  | Cl.8.1.2 | IS/IEC 60898-1 | 43 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | in this case, the operating means shall have two distinct rest positions corresponding to the position of the contacts but, for automatic opening, a third distinct position of the operating means may be provided. | Satisfactory or Not Satisfactory (doen't have 2 distinct position) |  | Cl.8.1.2 | IS/IEC 60898-1 | 44 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | The action of the mechanism shall not be influenced by the position of enclosures or covers and shall be independent of any removable part. | Satisfactory or Not Satisfactory (influenced by the position of enclosures or covers) |  | Cl.8.1.2 | IS/IEC 60898-1 | 45 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | If the cover is used as a guiding means for push-buttons, it shall not be possible to remove the buttons from the outside of the circuit-breaker. | Satisfactory or Not Satisfactory (possible to remove the buttons from the outside of the circuit-breaker) |  | Cl.8.1.2 | IS/IEC 60898-1 | 46 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | Operating means shall be securely fixed on their shafts and it shall not be possible to remove them without the aid of a tool. | Satisfactory or Not Satisfactory (possible to remove them without the aid of a tool) |  | Cl.8.1.2 | IS/IEC 60898-1 | 47 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | If the operating means has an "up-down" movement, when the circuit-breaker is mounted as in normal use, the contacts shall be closed by the up movement | Satisfactory or Not Satisfactory (contacts not closed by the up movement) |  | Cl.8.1.2 | IS/IEC 60898-1 | 48 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.2 | Mechanism | Yes | Mandatory | When means are provided or specified by the manufacturer to lock the operating means in the open position, locking in that position shall only be possible when the main contacts are in the open position. | Satisfactory or Not Satisfactory (locking possible even when the main contacts are not in the open position) |  | Cl.8.1.2 | IS/IEC 60898-1 | 49 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Clearance distances | Yes | Mandatory | between live parts which are separated when the main contacts are in the open position, mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Uimp | Annex B | IS/IEC 60898-1 | 1 | N.A | N.A | [47 empty] | 2 | - | 4 | - | 4 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Clearance distances | Yes | Mandatory | between live parts of different polarity, mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Uimp | Annex B | IS/IEC 60898-1 | 2 | N.A | N.A | [47 empty] | 1.5 | - | 3 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Clearance distances | Yes | Mandatory | between circuits supplied from different sources, one of which being PELV or SELV g | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Uimp | Annex B | IS/IEC 60898-1 | 3 | N.A | N.A | [47 empty] | 3 | - | 6 | - | 8 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Clearance distances | Yes | Mandatory | between live parts and – accessible surfaces of operating means , mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Uimp | Annex B | IS/IEC 60898-1 | 4 | N.A | N.A | [47 empty] | 1.5 | - | 3 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Clearance distances | Yes | Mandatory | between live parts and – screws or other means for fixing covers which have to be removed when mounting the circuit–breaker, mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Uimp | Annex B | IS/IEC 60898-1 | 5 | N.A | N.A | [47 empty] | 1.5 | - | 3 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Clearance distances | Yes | Mandatory | between live parts and – surface on which the circuit breaker is mounted b , mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Uimp | Annex B | IS/IEC 60898-1 | 6 | N.A | N.A | [47 empty] | 1.5 | - | 3 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Clearance distances | Yes | Mandatory | between live parts and –screws or other means for fixing the circuit breaker b, mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Uimp | Annex B | IS/IEC 60898-1 | 7 | N.A | N.A | [47 empty] | 1.5 | - | 3 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Clearance distances | Yes | Mandatory | between live parts and – metal covers or boxes b , mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Uimp | Annex B | IS/IEC 60898-1 | 8 | N.A | N.A | [47 empty] | 1.5 | - | 3 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Clearance distances | Yes | Mandatory | between live parts and – other accessible metal parts c , mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Uimp | Annex B | IS/IEC 60898-1 | 9 | N.A | N.A | [47 empty] | 1.5 | - | 3 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Clearance distances | Yes | Mandatory | between live parts and – metal frames supporting flush type circuit breakers , mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Uimp | Annex B | IS/IEC 60898-1 | 10 | N.A | N.A | [47 empty] | 1.5 | - | 3 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Creepage distances | Yes | Mandatory | between live parts which are separated when the main contacts are in the open position, mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Material Group, Working Voltage | Annex B | IS/IEC 60898-1 | 11 | N.A | N.A | [53 empty] | 1.2 | - | 2 | - | 4 | - | 4 | - | 0.9 | - | 2 | - | 4 | - | 4 | - | 0.6 | - | 2 | - | 4 | - | 4 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Creepage distances | Yes | Mandatory | between live parts of different polarity, mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Material Group, Working Voltage | Annex B | IS/IEC 60898-1 | 12 | N.A | N.A | [53 empty] | 1.2 | - | 1.5 | - | 3 | - | 4 | - | 0.9 | - | 1.5 | - | 3 | - | 3 | - | 0.6 | - | 1.5 | - | 3 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Creepage distances | Yes | Mandatory | between circuits supplied from different sources, one of which being PELV or SELV g | Number of decimal places - Value to be specified in Integers or whole numbers | Material Group, Working Voltage | Annex B | IS/IEC 60898-1 | 13 | N.A | N.A | [55 empty] | 3 | - | 6 | - | 8 | - |  |  | 3 | - | 6 | - | 8 | - |  |  | 3 | - | 6 | - | 8 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Creepage distances | Yes | Mandatory | between live parts and – accessible surfaces of operating means , mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Material Group, Rated Voltage | Annex B | IS/IEC 60898-1 | 14 | N.A | N.A | [77 empty] | 1.5 | - | 4 | - | 1.5 | - | 3 | - | 1.5 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Creepage distances | Yes | Mandatory | between live parts and – screws or other means for fixing covers which have to be removed when mounting the circuit–breaker, mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Material Group, Rated Voltage | Annex B | IS/IEC 60898-1 | 15 | N.A | N.A | [77 empty] | 1.5 | - | 4 | - | 1.5 | - | 3 | - | 1.5 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Creepage distances | Yes | Mandatory | between live parts and – surface on which the circuit breaker is mounted b , mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Material Group, Rated Voltage | Annex B | IS/IEC 60898-1 | 16 | N.A | N.A | [77 empty] | 1.5 | - | 4 | - | 1.5 | - | 3 | - | 1.5 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Creepage distances | Yes | Mandatory | between live parts and –screws or other means for fixing the circuit breaker b, mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Material Group, Rated Voltage | Annex B | IS/IEC 60898-1 | 17 | N.A | N.A | [77 empty] | 1.5 | - | 4 | - | 1.5 | - | 3 | - | 1.5 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Creepage distances | Yes | Mandatory | between live parts and – metal covers or boxes b , mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Material Group, Rated Voltage | Annex B | IS/IEC 60898-1 | 18 | N.A | N.A | [77 empty] | 1.5 | - | 4 | - | 1.5 | - | 3 | - | 1.5 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Creepage distances | Yes | Mandatory | between live parts and – other accessible metal parts c , mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Material Group, Rated Voltage | Annex B | IS/IEC 60898-1 | 19 | N.A | N.A | [77 empty] | 1.5 | - | 4 | - | 1.5 | - | 3 | - | 1.5 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.1.3 | Creepage distances | Yes | Mandatory | between live parts and – metal frames supporting flush type circuit breakers , mm, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Material Group, Rated Voltage | Annex B | IS/IEC 60898-1 | 20 | N.A | N.A | [77 empty] | 1.5 | - | 4 | - | 1.5 | - | 3 | - | 1.5 | - | 3 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.1 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | Connections, whether electrical or mechanical, shall withstand the mechanical stresses occurring in normal use. | Satisfactory or Not Satisfactory (didn't withstand the mechanical stresses) |  | Cl.8.1.4.1 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.1 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | Screws operated when mounting the circuit-breaker during installation shall not be of the thread-cutting type. | Satisfactory or Not Satisfactory (Screws operated when mounting the circuit-breaker during installation are of the thread-cutting type) |  | Cl.8.1.4.1 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.1 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | Test of reliability of screws, current-carrying parts and connections | Satisfactory or Not Satisfactory (connections became loose or their electrical function got impaired) | Type of terminals, Type of enclosures | Cl.9.4 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.1 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | Test of reliability of screws, current-carrying parts and connections | Satisfactory or Not Satisfactory (screwed connections worked loose or there was damage, such as breakage of screws or damage to the head slots, threads, washers or stirrups, that impaired the further use of the circuit-breaker. ) | Type of terminals, Type of enclosures | Cl.9.4 | IS/IEC 60898-1 | 4 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.1 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | Test of reliability of screws, current-carrying parts and connections | Satisfactory or Not Satisfactory (enclosures or covers were damaged ) | Type of terminals, Type of enclosures | Cl.9.4 | IS/IEC 60898-1 | 5 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.2 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | For screws in engagement with a thread of insulating material and which are operated when mounting the circuit breaker during installation, correct introduction of the screws into the screw hole or nut shall be ensured. | Satisfactory or Not Satisfactory (not ensured) | Type of terminals, Type of enclosures | Cl.8.1.4.2 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.3 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | Electrical connections shall be so designed that contact pressure is not transmitted through insulating material other than ceramic, pure mica or other material characteristics no less suitable unless there is sufficient resilience in the metallic parts to compensate for any possible shrinkage yielding of the insulating material. | Satisfactory or Not Satisfactory (dimesions changed) | Type of terminals, Type of enclosures | Cl.8.1.4.3 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.4 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | Current-carrying parts including parts intended for protective conductors, if any, shall be made of a metal having, under the conditions occurring in the equipment, mechanical strength, electrical conductivity and resistance to corrosion adequate for their intended use. | Satisfactory or Not Satisfactory (not adequate mechanical strength, electrical conductivity or resistance to corrosion ) | Type of terminals, Type of enclosures | Cl.8.1.4.4 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.4 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | Current-carrying parts including parts intended for protective conductors, if any, shall be made of a metal having, under the conditions occurring in the equipment, mechanical strength, electrical conductivity and resistance to corrosion adequate for their intended use. | Satisfactory or Not Satisfactory (not adequate mechanical strength, electrical conductivity or resistance to corrosion ) | Type of terminals, Type of enclosures | Cl.8.1.4.4 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.4 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | For small springs and the like and for inaccessible parts exposed to abrasion, a layer of grease may provide sufficient protection against rusting. Such parts are only subjected to the test if there is a doubt as to the effectiveness of the grease film, and in such a case the test is made without previous removal of the grease. | Satisfactory or Not Satisfactory (signs of rust) | Type of terminals, Type of enclosures | Cl.9.16 | IS/IEC 60898-1 | 2 | N.A | N.A | [29 empty] | - | 3 | - | 3.5 | - | 4.5 | - | 6 | - | 7.5 | - | 9 | - | 13 | - | 15 | - | 20
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.4.4 | Reliability of Screws current carrying parts and connections | Yes | Mandatory | Ferrous parts shall be adequately protected against rusting. | Satisfactory or Not Satisfactory (signs of rust) | Type of terminals, Type of enclosures | Cl.9.16 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.1 | Terminals for external conductors | Yes | Mandatory | Terminals for external conductors shall be such that the conductors may be connected so as to ensure that the necessary contact pressure is maintained permanently. During the test, the conductors shall not move noticeably in the terminal. Compliance is checked by inspection, by the tests of 9.5 for screw-type terminals, by specific tests for plug-in or bolt-on circuit-breakers included in the standard, or by the tests of Annex J or K, as relevant for the type of connection. | Satisfactory or Not Satisfactory (necessary contact pressure is not maintained permanently) | Type of terminals, Type of enclosures | 8.1.5.1 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.2 | Terminals for external conductors | Yes | Mandatory | Circuit-breakers shall be provided with: either terminals which shall allow the connection of copper conductors having nominal cross-sectional areas as shown in Table 5; | Satisfactory or Not Satisfactory (doenot allow the conductor) | Type of terminals, Type of enclosures | 8.1.5.2 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.2 | Terminals for external conductors | Yes | Mandatory | Circuit-breakers shall be provided with: or terminals for external untreated aluminium conductors and with aluminium screw-type terminals for use with copper or with aluminium conductors according to Annex L. | Satisfactory or Not Satisfactory (doenot allow the conductor) | Type of terminals, Type of enclosures | 8.1.5.2 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.3 | Terminals for external conductors | Yes | Mandatory | The means for clamping the conductor in the terminals shall not serve to fix any other component, although they may hold the terminals in place or prevent them from turning. | Satisfactory or Not Satisfactory (can be used to fix other components) | Type of terminals, Type of enclosures | 8.1.5.3 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.4 | Terminals for external conductors | Yes | Mandatory | Terminals for rated currents up to and including 32 A shall allow the conductors to be connected without special preparation. | Satisfactory or Not Satisfactory (doent allow the conductors to be connected without special preparation) | Type of terminals, Type of enclosures | 8.1.5.4 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.5 | Terminals for external conductors | Yes | Mandatory | Terminals shall have adequate mechanical strength. Screw and nuts for clamping the conductors shall have a metric ISO thread comparable in pitch and mechanical strength. | Satisfactory or Not Satisfactory (inadequate mechanical strength) | Type of terminals, Type of enclosures | 8.1.5.5 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.6 | Terminals for external conductors | Yes | Mandatory | Terminals shall be so designed that they clamp the conductor without undue damage to the conductor. | Satisfactory or Not Satisfactory ( conductors showed undue damage or severed wires) | Type of terminals, Type of enclosures | Cl.9.5.3 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.7 | Terminals for external conductors | Yes | Mandatory | Terminals shall be so designed that they clamp the conductor reliably and between metal surfaces. | Satisfactory or Not Satisfactory ( work loose from their fixings to circuit-breakers) | Type of terminals, Type of enclosures | Cl.9.5.2 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.8 | Terminals for external conductors | Yes | Mandatory | Terminals shall be so designed or positioned that neither a rigid solid conductor nor a wire of a stranded conductor can slip out while the clamping screws of nuts are tightened. | Satisfactory or Not Satisfactory (slipped out of terminal) | Type of terminals, Type of enclosures | 8.1.5.8 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.9 | Terminals for external conductors | Yes | Mandatory | Terminals shall be so fixed or located that, when the clamping screws or nuts are tightened or loosened, the terminals shall not work loose from their fixing to circuit-breakers. | Satisfactory or Not Satisfactory ( worked loose from their fixings to circuit-breakers) | Type of terminals, Type of enclosures | 8.1.5.9 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.10 | Terminals for external conductors | Yes | Mandatory | Clamping screws or nuts of terminals intended for the connection of protective conductors shall be adequately secured against accidental loosening. | Satisfactory or Not Satisfactory ( not secured against accidental loosening) | Type of terminals, Type of enclosures | 8.1.5.10 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.11 | Terminals for external conductors | Yes | Mandatory | Pillar terminals shall allow full insertion and reliable clamping of the conductor. | Satisfactory or Not Satisfactory ( doesnot allow full insertion and reliable clamping of the conductor) | Type of terminals, Type of enclosures | 8.1.5.11 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.5.12 | Terminals for external conductors | Yes | Mandatory | Screws and nuts of terminals intended for the connections of external conductors shall be in engagement with a metal thread and the screw shall not be of the tapping screw type. | Satisfactory or Not Satisfactory ( is of the tapping screw type.) | Type of terminals, Type of enclosures | Cl.8.1.5.12 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.6 | Non-interchangeability | Yes | Mandatory | For circuit-breakers intended to be mounted on bases forming a unit therewith (plug-in type or screw-in type) it shall not be possible, without the aid of a tool, to replace a circuit-breakerwhen mounted and wired as for normal use by another of the same make having a higher rated current. | Satisfactory or Not Satisfactory ( possible, without the aid of a tool) | Method of mounting, type of terminals | Cl.8.1.6 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.7.1 | Mechanical mounting of plug-in type circuit-breakers | Yes | Mandatory | The mechanical mounting of plug-in type circuit-breakers, the holding in position of which does not depend solely on their plug-in connection(s), shall be reliable and have adequate stability. | Satisfactory or Not Satisfactory ( not reliable or don't have adequate stability) | Method of mounting | Cl.8.1.7.1 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.7.2 | Mechanical mounting of plug-in type circuit-breakers | Yes | Mandatory | - Plug-in type circuit-breakers, the holding in position of which does not depend solely on their plug-in connection(s) | Satisfactory or Not Satisfactory ( not reliable or don't have adequate stability) | Method of mounting | Cl.8.1.7.1 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.1.7.3 | Mechanical mounting of plug-in type circuit-breakers | Yes | Mandatory | - Plug-in type circuit-breakers, the holding in position of which depends solely on their plug-in connection(s) | Satisfactory or Not Satisfactory ( not reliable or don't have adequate stability) | Method of mounting | Cl.8.1.7.1 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | For circuit-breakers other than those of the plug-in type, external parts, other than screws or other means for fixing covers and labels, which are accessible when the circuit-breakers are mounted and wired as for normal use, shall either be of insulating material or be lined throughout with insulating material, unless the live parts are within an internal enclosure of insulating material. | Satisfactory or Not Satisfactory (not insulating material or not lined with insulating material) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | Linings shall be fixed in such a way that they are not likely to be lost during installation of the circuit-breakers. | Satisfactory or Not Satisfactory (likely to be lost during installation) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | They shall have adequate thickness | Satisfactory or Not Satisfactory (not adequate thickness) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | They shall have adequate mechanical strength | Satisfactory or Not Satisfactory (not adequate mechanical strength) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 4 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | They shall provide adequate protection at places where sharp edges occur. | Satisfactory or Not Satisfactory (no adequate protection) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 5 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | Inlet openings for cables or conduits shall either be of insulating material or be provided with bushings or similar devices of insulating material. | Satisfactory or Not Satisfactory ( no insulating material or no bushings or no similar devices of insulating material) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 6 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | Such devices shall be reliably fixed | Satisfactory or Not Satisfactory ( not reliably fixes) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 7 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | Such devices shall have adequate mechanical strength. | Satisfactory or Not Satisfactory (inadequate mechanical strength) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 8 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | For plug-in circuit-breakers, external parts other than screws or other means for fixing covers, which are accessible in normal conditions of use, shall be of insulating material. | Satisfactory or Not Satisfactory (not of insulating material) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 9 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | Metallic operating means shall be insulated from live parts | Satisfactory or Not Satisfactory (not insulated) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 10 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | their exposed conductive parts shall be covered by insulating material. | Satisfactory or Not Satisfactory (not covered) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 11 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | It shall be possible to replace plug-in circuit-breakers easily without touching live parts. | Satisfactory or Not Satisfactory (not possible) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals | 8.2 | IS/IEC 60898-1 | 12 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | The test finger is applied in every possible bending position of a real finger, an electrical contact indicator being used to show contact with live parts. | Satisfactory or Not Satisfactory (enclosures or covers deformed to such an extent that live parts can be touched with the unjointed test finger.) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals, Method of mounting | Cl.9.6 | IS/IEC 60898-1 | 13 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | Circuit-breakers with enclosures or covers of thermoplastic material are subjected to the following additional test, which is carried out at an ambient temperature of 35 °C ± 2 °C, the circuit-breakers being at this temperature. The circuit-breakers are subjected for 1 min to a force of 75 N, applied through the tip of a straight unjointed test finger of the same dimensions as the standard test finger. This finger is applied to all places where yielding of insulating material could impair the safety of the circuit breaker, but is not applied to knock-outs. | Satisfactory or Not Satisfactory (enclosures or covers deformed to such an extent that live parts can be touched with the unjointed test finger.) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals, Method of mounting | Cl.9.6 | IS/IEC 60898-1 | 14 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.2 | Protection against Electric Shock | Yes | Mandatory | Unenclosed circuit-breakers having parts not intended to be covered by an enclosure are submitted to the test with a metal front panel, and mounted as for normal use. | Satisfactory or Not Satisfactory (enclosures or covers deformed to such an extent that live parts can be touched with the unjointed test finger.) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Type of terminals, Method of mounting | Cl.9.6 | IS/IEC 60898-1 | 15 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Resistance to humidity | Satisfactory or Not Satisfactory (sample got damaged) |  | Cl.9.7.1 | IS/IEC 60898-1 | 1 | N.A | N.A | [20 empty] | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Insulation resistance of the main circuit - a) with the circuit-breaker in the open position, between each pair of the terminals which are electrically connected together when the circuit-breaker is in the closed position, in turn on each pole; MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers |  | Cl.9.7.2 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Insulation resistance of the main circuit - b) with the circuit-breaker in the closed position, between each pole and the others connected together;; MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers |  | Cl.9.7.2 | IS/IEC 60898-1 | 3 | N.A | N.A |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Insulation resistance of the main circuit - c) with the circuit-breaker in the closed position, between all poles connected together and the frame, including a metal foil or part in contact with the outer surface of the housing of insulating material but with the terminal areas kept completely free to avoid flashover between terminals and the metal foil; ; MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers |  | Cl.9.7.2 | IS/IEC 60898-1 | 4 | N.A | N.A |  | - | 5 | - | 5 |  |  |  |  | - | 5 | - | 5 |  |  |  |  | - | 5 | - | 5
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Insulation resistance of the main circuit - ad) between metal parts of the mechanism and the frame;; MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers |  | Cl.9.7.2 | IS/IEC 60898-1 | 5 | N.A | N.A |  | - | 5 | - | 5 |  |  |  |  | - | 5 | - | 5 |  |  |  |  | - | 5 | - | 5
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Insulation resistance of the main circuit - e) for circuit-breakers with a metal enclosure having an internal lining of insulating material, between the frame and a metal foil in contact with the inner surface of the lining of insulating material,l including bushings and similar devices. MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers |  | Cl.9.7.2 | IS/IEC 60898-1 | 6 | N.A | N.A |  | - | 5 | - | 5 |  |  |  |  | - | 5 | - | 5 |  |  |  |  | - | 5 | - | 5
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Dielectric strength of the main circuit - a) with the circuit-breaker in the open position, between each pair of the terminals which are electrically connected together when the circuit-breaker is in the closed position, in turn on each pole; test voltage - 2000 V | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.3 | IS/IEC 60898-1 | 7 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Dielectric strength of the main circuit - b) with the circuit-breaker in the closed position, between each pole and the others connected together; test voltage - 2000 V | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.3 | IS/IEC 60898-1 | 8 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Dielectric strength of the main circuit - c) with the circuit-breaker in the closed position, between all poles connected together and the frame, including a metal foil or part in contact with the outer surface of the housing of insulating material but with the terminal areas kept completely free to avoid flashover between terminals and the metal foil; test voltage - 2000 V | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.3 | IS/IEC 60898-1 | 9 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Dielectric strength of the main circuit - d) between metal parts of the mechanism and the frame; test voltage - 2000 V | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.3 | IS/IEC 60898-1 | 10 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Dielectric strength of the main circuit - e) for circuit-breakers with a metal enclosure having an internal lining of insulating material, between the frame and a metal foil in contact with the inner surface of the lining of insulating material,l including bushings and similar devices. test voltage - 2500 V | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.3 | IS/IEC 60898-1 | 11 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Insulation resistance and dielectric strength of auxiliary circuits - between the auxiliary circuits connected to each other and to the frame; MΩ, Max | Number of decimal places - Value upto 1 decimal places | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.4 | IS/IEC 60898-1 | 12 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - between each of the parts of the auxiliary circuits which might be isolated from the other parts in normal service and the whole of the other parts connected together, at a voltage of approximately 500 V d.c., after this voltage has been applied for 1 min.; MΩ, Max | Number of decimal places - Value upto 1 decimal places | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.4 | IS/IEC 60898-1 | 13 | N.A | N.A |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - Insulation resistance and dielectric strength of auxiliary circuits - A substantially sinusoidal voltage at rated frequency is applied for 1 min - between the auxiliary circuits connected to each other and to the frame; | Satisfactory or Not Satisfactory (flashover or perforation occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.4 | IS/IEC 60898-1 | 14 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.2 | Dielectric strength at power frequency | Yes | Mandatory | Circuit-breakers shall have adequate dielectric properties at power frequency - A substantially sinusoidal voltage at rated frequency is applied for 1 min - between each of the parts of the auxiliary circuits which might be isolated from the other parts in normal service and the whole of the other parts connected together, at a voltage of approximately 500 V d.c., after this voltage has been applied for 1 min.; | Satisfactory or Not Satisfactory (flashover or perforation occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.4 | IS/IEC 60898-1 | 15 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.3.3 | Isolating capability | Yes | Mandatory | Circuit-breakers shall be suitable for isolation - minimum clearances - between live parts which are separated when the main contacts are in the open position, mm | Number of decimal places - Value upto 1 decimal places | Rated Voltage, Working Voltage, Impulse Voltage, Material Group, Pollution Degree | Annex B | IS/IEC 60898-1 | 1 | N.A | N.A | [47 empty] | 2 | - | 4 | - | 4 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.3.3 | Isolating capability | Yes | Mandatory | Circuit-breakers shall be suitable for isolation - minimum creepage - between live parts which are separated when the main contacts are in the open position, mm | Number of decimal places - Value upto 1 decimal places | Rated Voltage, Working Voltage, Impulse Voltage, Material Group, Pollution Degree | Annex B | IS/IEC 60898-1 | 2 | N.A | N.A | [53 empty] | 1.2 | - | 2 | - | 4 | - | 4 | - | 0.9 | - | 2 | - | 4 | - | 4 | - | 0.6 | - | 2 | - | 4 | - | 4 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.3 | Isolating capability | Yes | Mandatory | Verification of impulse withstand voltages (across clearances and across solid insulation) and of leakage current across open contacts - For each test, five positive impulses and five negative impulses are applied. The interval between consecutive impulses being at least 1 s for impulses of the same polarity and being at least 10 s for impulses of the opposite polarity. | Satisfactory or Not Satisfactory (disruptive discharge (sparkover, flashover or puncture) occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.5.1 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.3.3 | Isolating capability | Yes | Mandatory | Verification of impulse withstand voltages (across clearances and across solid insulation) and of leakage current across open contacts - Verification of leakage currents across open contacts (suitability for isolation); mA, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn) | Cl.9.7.5.3 | IS/IEC 60898-1 | 4 | N.A | N.A |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.4 | Dielectric strength at rated impulse withstand voltage (Uimp) | Yes | Mandatory | Circuit-breakers shall adequately withstand impulse voltages - Verification of clearances with the impulse withstand voltage - A first series of tests is made applying the impulse voltage between: the phase pole(s) and the neutral pole (or path) connected together, | Satisfactory or Not Satisfactory (disruptive discharge occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Impulse Voltage, Sea Level | Cl.9.7.5.2 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.4 | Dielectric strength at rated impulse withstand voltage (Uimp) | Yes | Mandatory | Circuit-breakers shall adequately withstand impulse voltages - Verification of clearances with the impulse withstand voltage - A first series of tests is made applying the impulse voltage between: and the metal support connected to the terminal(s) intended for the protective conductor(s), if any. | Satisfactory or Not Satisfactory (disruptive discharge occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Impulse Voltage, Sea Level | Cl.9.7.5.2 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.4 | Dielectric strength at rated impulse withstand voltage (Uimp) | Yes | Mandatory | Circuit-breakers shall adequately withstand impulse voltages - Verification of clearances with the impulse withstand voltage - A second series of tests is made applying the impulse voltage between: the phase pole(s), connected together, , | Satisfactory or Not Satisfactory (disruptive discharge occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Impulse Voltage, Sea Level | Cl.9.7.5.2 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.4 | Dielectric strength at rated impulse withstand voltage (Uimp) | Yes | Mandatory | Circuit-breakers shall adequately withstand impulse voltages - Verification of clearances with the impulse withstand voltage - A third series of tests is made applying the impulse voltage between: b) with the circuit-breaker in the closed position, between each pole and the others connected together; | Satisfactory or Not Satisfactory (disruptive discharge occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Impulse Voltage, Sea Level | Cl.9.7.5.2 | IS/IEC 60898-1 | 4 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.4 | Dielectric strength at rated impulse withstand voltage (Uimp) | Yes | Mandatory | Circuit-breakers shall adequately withstand impulse voltages - Verification of clearances with the impulse withstand voltage - A third series of tests is made applying the impulse voltage between: c) with the circuit-breaker in the closed position, between all poles connected together and the frame, including a metal foil or part in contact with the outer surface of the housing of insulating material but with the terminal areas kept completely free to avoid flashover between terminals and the metal foil; | Satisfactory or Not Satisfactory (disruptive discharge occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Impulse Voltage, Sea Level | Cl.9.7.5.2 | IS/IEC 60898-1 | 5 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.4 | Dielectric strength at rated impulse withstand voltage (Uimp) | Yes | Mandatory | Circuit-breakers shall adequately withstand impulse voltages - Verification of clearances with the impulse withstand voltage - A third series of tests is made applying the impulse voltage between: d) between metal parts of the mechanism and the frame; | Satisfactory or Not Satisfactory (disruptive discharge occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Impulse Voltage, Sea Level | Cl.9.7.5.2 | IS/IEC 60898-1 | 6 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.4 | Dielectric strength at rated impulse withstand voltage (Uimp) | Yes | Mandatory | Circuit-breakers shall adequately withstand impulse voltages - Verification of clearances with the impulse withstand voltage - A third series of tests is made applying the impulse voltage between: e) for circuit-breakers with a metal enclosure having an internal lining of insulating material, between the frame and a metal foil in contact with the inner surface of the lining of insulating material,l including bushings and similar devices. | Satisfactory or Not Satisfactory (disruptive discharge occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Impulse Voltage, Sea Level | Cl.9.7.5.2 | IS/IEC 60898-1 | 7 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.3.4 | Dielectric strength at rated impulse withstand voltage (Uimp) | Yes | Mandatory | If, however, only one such disruptive discharge occurs, ten additional impulses having the same polarity as that which caused the disruptive discharge are applied, the connections being the same as those with which the failure occurred. | Satisfactory or Not Satisfactory (disruptive discharge occured) | Rated Voltage, Rated Current (In), Rated short-circuit capacity (Icn), Impulse Voltage, Sea Level | Cl.9.7.5.2 | IS/IEC 60898-1 | 8 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.4.1 | Temperature-rise | Yes | Mandatory | Temperature-rise -- Terminals for external connections, K, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Current (In), No. of Poles | Cl.9.8.2 | IS/IEC 60898-1 | 1 | N.A | N.A |  | - | 60 | - | 60 |  |  |  |  | - | 60 | - | 60 |  |  |  |  | - | 60 | - | 60
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.4.1 | Temperature-rise | Yes | Mandatory | Temperature-rise -- External parts liable to be touched during manual operation of the circuit-breaker, K, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Current (In), No. of Poles | Cl.9.8.2 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 40 | - | 40 |  |  |  |  | - | 40 | - | 40 |  |  |  |  | - | 40 | - | 40
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.4.1 | Temperature-rise | Yes | Mandatory | Temperature-rise -- External metallic parts of operating means, K, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Current (In), No. of Poles | Cl.9.8.2 | IS/IEC 60898-1 | 3 | N.A | N.A |  | - | 25 | - | 25 |  |  |  |  | - | 25 | - | 25 |  |  |  |  | - | 25 | - | 25
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.4.1 | Temperature-rise | Yes | Mandatory | Temperature-rise -- Other external parts, K, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Current (In), No. of Poles | Cl.9.8.2 | IS/IEC 60898-1 | 4 | N.A | N.A |  | - | 60 | - | 60 |  |  |  |  | - | 60 | - | 60 |  |  |  |  | - | 60 | - | 60
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.4.1 | Temperature-rise | Yes | Mandatory | The circuit-breaker shall not suffer damage impairing its functions and its safe use. | Satisfactory or Not Satisfactory (circuit-breaker suffered damage impairing its functions and its safe use) | Rated Current (In), No. of Poles | Cl.8.4.1 | IS/IEC 60898-1 | 5 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.4.2 | Temperature-rise | Yes | Mandatory | Ambient air temperature - The ambient air temperature does not exceed +40 °C; The lower limit of the ambient air temperature is –5 °C; °C | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Current (In), No. of Poles | Cl.7.2 | IS/IEC 60898-1 | 1 | N.A | N.A |  | -5 | 40 | -5 | 40 |  |  |  |  | -5 | 40 | -5 | 40 |  |  |  |  | -5 | 40 | -5 | 40
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.4.2 | Temperature-rise | Yes | Mandatory | Ambient air temperature - its average over a period of 24 h does not exceed +35 °C.; °C, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Current (In), No. of Poles | Cl.7.2 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 35 | - | 35 |  |  |  |  | - | 35 | - | 35 |  |  |  |  | - | 35 | - | 35
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.5 | Uninterrupted duty | Yes | Mandatory | Circuit-breakers shall operate reliably even after long service. | Satisfactory or Not Satisfactory (doesn't operate reliably) | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.8.5 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.5 | Uninterrupted duty - 28 day test | Yes | Mandatory | The circuit-breaker is subjected to 28 cycles, each cycle comprising 21 h with a current equal to the rated current at an open circuit voltage of at least 30 V, and 3 h without current under the test conditions of 9.2. The circuit-breaker is in the closed position, the current being established and interrupted by an auxiliary switch., sec, Max | Number of decimal places - Value to be specified in Integers or whole numbers | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.9 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.5 | Uninterrupted duty - 28 day test | Yes | Mandatory | During the last period of current flow the temperature-rise of the terminals shall be measured - Terminals for external connections, K, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Number of decimal places - Value to be specified in Integers or whole numbers | Cl.9.9 | IS/IEC 60898-1 | 3 | N.A | N.A |  | - | 15 | - | 15 |  |  |  |  | - | 15 | - | 15 |  |  |  |  | - | 15 | - | 15
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.5 | Uninterrupted duty - 28 day test | Yes | Mandatory | During the last period of current flow the temperature-rise of the terminals shall be measured - External parts liable to be touched during manual operation of the circuit-breaker, including operating means of insulating material and metallic means for coupling insulated operating means of several poles, K, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Number of decimal places - Value to be specified in Integers or whole numbers | Cl.9.9 | IS/IEC 60898-1 | 4 | N.A | N.A |  | - | 15 | - | 15 |  |  |  |  | - | 15 | - | 15 |  |  |  |  | - | 15 | - | 15
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.5 | Uninterrupted duty - 28 day test | Yes | Mandatory | During the last period of current flow the temperature-rise of the terminals shall be measured - External metallic parts of operating means, K, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Number of decimal places - Value to be specified in Integers or whole numbers | Cl.9.9 | IS/IEC 60898-1 | 5 | N.A | N.A |  | - | 15 | - | 15 |  |  |  |  | - | 15 | - | 15 |  |  |  |  | - | 15 | - | 15
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.5 | Uninterrupted duty - 28 day test | Yes | Mandatory | During the last period of current flow the temperature-rise of the terminals shall be measured - Other external parts, including that face of the circuit-breaker in direct contact with the mounting surface, K, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Number of decimal places - Value to be specified in Integers or whole numbers | Cl.9.9 | IS/IEC 60898-1 | 6 | N.A | N.A |  | - | 15 | - | 15 |  |  |  |  | - | 15 | - | 15 |  |  |  |  | - | 15 | - | 15
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.5 | Uninterrupted duty - 28 day test | Yes | Mandatory | Immediately after this measurement of the temperature-rise, the current is steadily increased within 5 s to the conventional tripping current, sec, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Number of decimal places - Value to be specified in Integers or whole numbers | Cl.9.9 | IS/IEC 60898-1 | 7 | N.A | N.A |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.6.1 | Automatic operation - Standard time-current zone | Yes | Mandatory | The tripping characteristic of circuit-breakers shall be such that they ensure adequate protection of the circuit, without premature operation. | Satisfactory or Not Satisfactory (inadequate protection of the circuit) | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.8.6.1 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.1 | Automatic operation - Test of time-current characteristic | Yes | Mandatory | Test a, hr, Max | Number of decimal places - Value to be specified in Integers or whole numbers | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.2.1 | IS/IEC 60898-1 | 1 | N.A | N.A |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.1 | Automatic operation - Test of time-current characteristic | Yes | Mandatory | Test b, hr, Max | Number of decimal places - Value to be specified in Integers or whole numbers | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.2.1 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.1 | Automatic operation - Test of time-current characteristic | Yes | Mandatory | Test c, sec | Number of decimal places - Value to be specified in Integers or whole numbers | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.2.2 | IS/IEC 60898-1 | 3 | N.A | N.A | [5 empty] | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.1 | Automatic operation - Test of instantaneous tripping, of correct opening of the contacts and of the trip-free function | Yes | Mandatory | Test d - For circuit-breakers of the B-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.2 | IS/IEC 60898-1 | 4 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.1 | Automatic operation - Test of instantaneous tripping, of correct opening of the contacts and of the trip-free function | Yes | Mandatory | Test e - For circuit-breakers of the B-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.2 | IS/IEC 60898-1 | 5 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.1 | Automatic operation - Test of instantaneous tripping, of correct opening of the contacts and of the trip-free function | Yes | Mandatory | Test d - For circuit-breakers of the C-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.3 | IS/IEC 60898-1 | 6 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.1 | Automatic operation - Test of instantaneous tripping, of correct opening of the contacts and of the trip-free function | Yes | Mandatory | Test e - For circuit-breakers of the C-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.3 | IS/IEC 60898-1 | 7 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.1 | Automatic operation - Test of instantaneous tripping, of correct opening of the contacts and of the trip-free function | Yes | Mandatory | Test d - For circuit-breakers of the D-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.4 | IS/IEC 60898-1 | 8 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.1 | Automatic operation - Test of instantaneous tripping, of correct opening of the contacts and of the trip-free function | Yes | Mandatory | Test e - For circuit-breakers of the D-type, sec, Max | Number of decimal places - Value upto 1 decimal places | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.3.4 | IS/IEC 60898-1 | 9 | N.A | N.A |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.2 | Automatic operation - Effect of single-pole loading of multipole circuit-breakers on the tripping characteristic | Yes | Mandatory | When circuit-breakers having more than one protected pole are loaded on only one of the protected poles, starting from cold, with a current equal to 1,1 times the conventional tripping current, for two-pole circuit-breakers with two protected poles, hr, Max | Number of decimal places - Value to be specified in Integers or whole numbers | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.4 | IS/IEC 60898-1 | 1 | N.A | N.A |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.2 | Automatic operation - Effect of single-pole loading of multipole circuit-breakers on the tripping characteristic | Yes | Mandatory | When circuit-breakers having more than one protected pole are loaded on only one of the protected poles, starting from cold, with a current equal to 1,2 times the conventional tripping current, for three-pole and four-pole circuit-breakers, hr, Max | Number of decimal places - Value to be specified in Integers or whole numbers | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.4 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.3 | Automatic operation - Effect of the ambient air temperature on the tripping characteristic | Yes | Mandatory | The circuit-breaker is placed in an ambient temperature of (35 ± 2) K below the ambient air reference temperature until it has attained steady-state temperature. A current equal to 1,13 In (conventional non-tripping current) is passed through all poles for the conventional time. The current is then steadily increased within 5 s to 1,9 In, hr, Max | Number of decimal places - Value to be specified in Integers or whole numbers | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.5 a) | IS/IEC 60898-1 | 1 | N.A | N.A |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.6.3.3 | Automatic operation - Effect of the ambient air temperature on the tripping characteristic | Yes | Mandatory | The circuit-breaker is placed in an ambient temperature of (10 ± 2) K above the ambient air reference temperature until it has attained steady-state temperature. A current equal to In is passed through all poles, hr, Max | Number of decimal places - Value to be specified in Integers or whole numbers | No. of Poles, Type of Enclosures, Rated Current (In), Type | Cl.9.10.5 b) | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.7 | Mechanical and electrical endurance - Verification of mechanical and electrical endurance | Yes | Mandatory | The circuit-breaker is submitted to 4 000 operating cycles with rated current; Each operating cycle consists of a making operation followed by a breaking operation; For circuit-breakers of rated current up to and including 32 A the operating frequency shall be 240 operating cycles per hour. During each operating cycle, the circuit-breaker shall remain open for at least 13 s. | Satisfactory or Not Satisfactory (sample shows undue wear or discrepancy between the position of the moving contacts and of the corresponding position of the indicating device or damage to the enclosure permitting access to live parts by the test finger or loosening of electrical or or mechanical connections orseepage of sealing compound) | No. of Poles, Type of Enclosures, Rated Current (In), Rated Voltage | Cl.9.11.2 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.7 | Mechanical and electrical endurance - Verification of mechanical and electrical endurance | Yes | Mandatory | The circuit-breaker is submitted to 4 000 operating cycles with rated current; Each operating cycle consists of a making operation followed by a breaking operation; For circuit-breakers of rated current above 32 A the operating frequency shall be 120 operating cycles per hour. During each operating cycle the circuit-breaker shall remain open for at least 28 s. | Satisfactory or Not Satisfactory (sample shows undue wear or discrepancy between the position of the moving contacts and of the corresponding position of the indicating device or damage to the enclosure permitting access to live parts by the test finger or loosening of electrical or or mechanical connections orseepage of sealing compound) | No. of Poles, Type of Enclosures, Rated Current (In), Rated Voltage | Cl.9.11.2 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.11.3 | Mechanical and electrical endurance - Verification of mechanical and electrical endurance | Yes | Mandatory | Moreover, the circuit-breaker shall comply with the test of 9.10.2.2 - A current equal to 2,55 In is passed through all poles, starting from cold, sec | Number of decimal places - Value to be specified in Integers or whole numbers | No. of Poles, Type of Enclosures, Rated Current (In), Rated Voltage | Cl.9.10.2.2 | IS/IEC 60898-1 | 1 | N.A | N.A | [5 empty] | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.11.3 | Mechanical and electrical endurance - Verification of mechanical and electrical endurance | Yes | Mandatory | shall withstand the dielectric strength test according to 9.7.3, but at a voltage 500 V less than the value prescribed in 9.7.4 and without previous humidity treatment. | Satisfactory or Not Satisfactory (flashover or breakdown occured) | No. of Poles, Type of Enclosures, Rated Current (In), Rated Voltage | Cl.9.7.3 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents - Power factor of the test circuit | Yes | Mandatory | Method 1 – Determination from d.c. component, Single Phase, Power factor | Number of decimal places - Value upto 2 decimal places | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.5, Annex A.2 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents - Power factor of the test circuit | Yes | Mandatory | Method 2 – Determination with pilot generator, Single Phase, Power factor | Number of decimal places - Value upto 2 decimal places | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.5, Annex A.2 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents - Power factor of the test circuit | Yes | Mandatory | Method 1 – Determination from d.c. component, Poly Phase, Power factor | Number of decimal places - Value upto 2 decimal places Number of observations - Average of 3 readings | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.5, Annex A.3 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents - Power factor of the test circuit | Yes | Mandatory | Method 2 – Determination with pilot generator, Poly Phase, Power factor | Number of decimal places - Value upto 2 decimal places Number of observations - Average of 3 readings | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.5, Annex A.3 | IS/IEC 60898-1 | 4 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | It is also required that the corresponding values of I2t lie below the I2t characteristic. | Satisfactory or Not Satisfactory (is more than that declared by the manufacturer) | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.6 | IS/IEC 60898-1 | 5 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | I2t, A | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.6 | IS/IEC 60898-1 | 6 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Ip, A | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.6 | IS/IEC 60898-1 | 7 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Applied recovery voltages, V | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.8.1 | IS/IEC 60898-1 | 8 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Power frequency recovery voltages, V | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.8.1 | IS/IEC 60898-1 | 9 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Voltage on the supply side, V | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.8.1 | IS/IEC 60898-1 | 10 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Prospective short-circuit current, A | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.8.2 | IS/IEC 60898-1 | 11 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Prospective short-circuit current, poly phase, A | Number of decimal places - Value to be specified in Integers or whole numbers Number of observations - Average of 3 readings | Rated Voltage, No. of Poles, Rated short-circuit capacity (Icn) | Cl.9.12.8.2 | IS/IEC 60898-1 | 12 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test on all circuit-breakers: O – t – O – t – O – t – O – t – O – t- O – t – CO – t – CO – t – CO | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.2.1 | IS/IEC 60898-1 | 13 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Short-circuit test on circuit-breakers rated 230 V, or 240 V or 230/400 V for verifying their suitability for use in IT systems: O – t – CO | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.2.2 | IS/IEC 60898-1 | 14 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the tests according to 9.12.11.2, 9.12.11.3 or 9.12.11.4.2, the circuit-breakers shall show no damage impairing their further use | Satisfactory or Not Satisfactory (damaged impairing further use) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.1 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Verification of leakage currents across open contacts (suitability for isolation), leakage current, mA, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.5.3 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Dielectric strength tests according to 9.7.3, carried out between 2 h and 24 h after the short-circuit tests at a voltage of 500 V less than the value prescribed in 9.7.5 and without previous humidity treatment. | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.3 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the test carried out under the conditions specified in item a) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 a) | IS/IEC 60898-1 | 4 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | During the test carried out under the conditions specified in item b) of 9.7.2 | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 b) | IS/IEC 60898-1 | 5 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at 1 500 A: For three-pole circuit-breakers, no connection G1 is made between the neutral of the supply and the common point, if any, on the load side of the circuit-breaker. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.3 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at 1 500 A: For four-pole circuit-breakers with three protected poles, the neutral of the supply is connected through the unprotected pole or the switched neutral pole to the common point on the load side of the circuit-breaker. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.3 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at 1 500 A: If the neutral of a four-pole circuit-breaker is not marked by the manufacturer, the tests are repeated with three new samples, using successively each pole as neutral in turn. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.3 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at 1 500 A: For the test of single-pole circuit-breakers, the auxiliary switch T is synchronized with respect to the voltage wave so that the six points of initiation are equally distributed over the half-wave with a tolerance of ±5°. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.3 | IS/IEC 60898-1 | 4 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at 1 500 A: For the test of two-pole circuit-breakers, the auxiliary switch T is synchronized with respect to the voltage wave so that the six points of initiation are equally distributed over the half-wave with a tolerance of ±5°. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.3 | IS/IEC 60898-1 | 5 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at 1 500 A: The sequence of operations shall be as specified in 9.12.11.2, | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.3 | IS/IEC 60898-1 | 6 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at 1 500 A: except for single-pole circuit breakers of rated voltage 230/400 V. In that case only two CO operations are performed following the six O operations; in addition single-pole circuit-breakers are then tested by performing simultaneously one O operation, one circuit-breaker being inserted in each phase of the test circuit specified for three-pole circuit-breakers (Figure 3), without synchronization of the auxiliary switch establishing the short-circuit. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.3 | IS/IEC 60898-1 | 7 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at 1 500 A: For three-pole and four-pole circuit-breakers, random point-on-wave testing is acceptable. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.3 | IS/IEC 60898-1 | 8 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the tests according to 9.12.11.2, 9.12.11.3 or 9.12.11.4.2, the circuit-breakers shall show no damage impairing their further use | Satisfactory or Not Satisfactory (damaged impairing further use) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.1 | IS/IEC 60898-1 | 1 | N.A | N.A |  | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Verification of leakage currents across open contacts (suitability for isolation), leakage current, mA, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.5.3 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Dielectric strength tests according to 9.7.3, carried out between 2 h and 24 h after the short-circuit tests at a voltage of 500 V less than the value prescribed in 9.7.5 and without previous humidity treatment. | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.3 | IS/IEC 60898-1 | 3 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the test carried out under the conditions specified in item a) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 a) | IS/IEC 60898-1 | 4 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the test carried out under the conditions specified in item b) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 b) | IS/IEC 60898-1 | 5 | N.A | N.A |  | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Moreover, the circuit-breakers shall not trip when a current equal to 0,85 times the conventional non-tripping current is passed through all poles for the conventional time, starting from cold. At the end of this verification the current is steadily increased, within 5 s, to 1,1 times the conventional tripping current. The circuit-breakers shall trip within the conventional time, sec, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.1 | IS/IEC 60898-1 | 6 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at service short-circuit capacity (Ics) - two-pole - O – t – O – t – CO | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.4.2 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at service short-circuit capacity (Ics) - three-pole - O – t – CO – t – CO | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.4.2 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at service short-circuit capacity (Ics) - four-pole - O – t – CO – t – CO | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.4.2 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at service short-circuit capacity (Ics) - For single-pole circuit-breakers of rated voltage 230/400 V an additional set of three samples is tested in a circuit according to Figure 3 without N- connection | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.4.2 | IS/IEC 60898-1 | 4 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the tests according to 9.12.11.2, 9.12.11.3 or 9.12.11.4.2, the circuit-breakers shall show no damage impairing their further use | Satisfactory or Not Satisfactory (damaged impairing further use) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.1 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Verification of leakage currents across open contacts (suitability for isolation), leakage current, mA, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.5.3 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Dielectric strength tests according to 9.7.3, carried out between 2 h and 24 h after the short-circuit tests at a voltage of 500 V less than the value prescribed in 9.7.5 and without previous humidity treatment. | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.3 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the test carried out under the conditions specified in item a) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 a) | IS/IEC 60898-1 | 4 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the test carried out under the conditions specified in item b) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 b) | IS/IEC 60898-1 | 5 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.1 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Moreover, the circuit-breakers shall not trip when a current equal to 0,85 times the conventional non-tripping current is passed through all poles for the conventional time, starting from cold. At the end of this verification the current is steadily increased, within 5 s, to 1,1 times the conventional tripping current. The circuit-breakers shall trip within the conventional time, sec, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.1 | IS/IEC 60898-1 | 6 | N.A | N.A |  | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at rated short-circuit capacity (Icn) - O – t – CO | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.4.3 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at rated short-circuit capacity (Icn) - For multipole circuit-breakers the same pole shall be used as reference for the purpose of synchronization - O – t – CO | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.4.3 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at rated short-circuit capacity (Icn) - For single-pole circuit-breakers of rated voltage 230/400 V an additional set of four samples is tested in a circuit according to Figure 3 without N- connection | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.4.3 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the tests according to 9.12.11.4.3 and 9.12.11.4.4 the polyethylene foil shall show no holes visible with normal or corrected vision without additional magnification and the circuit breakers shall show no damage impairing their further use | Satisfactory or Not Satisfactory (the polyethylene foil shows holes visible with normal or corrected vision without additional magnification or the circuit breakers shows damage impairing their further use) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.2 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Verification of leakage currents across open contacts (suitability for isolation), leakage current, mA, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.5.3 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Dielectric strength tests according to 9.7.3, carried out between 2 h and 24 h after the short-circuit tests at a voltage of 900 V and without previous humidity treatment. | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.3 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the test carried out under the conditions specified in item a) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 a) | IS/IEC 60898-1 | 4 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the test carried out under the conditions specified in item b) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 b) | IS/IEC 60898-1 | 5 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Moreover the circuit-breakers shall trip within the time corresponding to the test c of Table 7 when a current equal to 2,8 In is passed through all poles, the lower time limit being 0,1 s instead of 1 s, sec, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.2 | IS/IEC 60898-1 | 6 | N.A | N.A |  | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | The sample shown as number 1 in Table 23 is not subjected to the verification of this subclause, but it shall nevertheless comply with the requirements of 9.12.10. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.2 | IS/IEC 60898-1 | 7 | N.A | N.A | [5 empty] | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.8 | Performance at short-circuit currents | Yes | Mandatory | Test at the making and breaking capacity on an individual pole (Icn1) of multipole circuit-breakers - O – t – CO | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.11.4.4 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the tests according to 9.12.11.4.3 and 9.12.11.4.4 the polyethylene foil shall show no holes visible with normal or corrected vision without additional magnification and the circuit breakers shall show no damage impairing their further use | Satisfactory or Not Satisfactory (the polyethylene foil shows holes visible with normal or corrected vision without additional magnification or the circuit breakers shows damage impairing their further use) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | 9.12.12.2 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Verification of leakage currents across open contacts (suitability for isolation), leakage current, mA, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.5.3 | IS/IEC 60898-1 | 2 | N.A | N.A |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2 |  |  |  |  | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Dielectric strength tests according to 9.7.3, carried out between 2 h and 24 h after the short-circuit tests at a voltage of 900 V and without previous humidity treatment. | Satisfactory or Not Satisfactory (flashover or breakdown occured) | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.3 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the test carried out under the conditions specified in item a) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 a) | IS/IEC 60898-1 | 4 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | After the test carried out under the conditions specified in item b) of 9.7.2, Insulation resistance, MΩ, Min | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.7.2 b) | IS/IEC 60898-1 | 5 | N.A | N.A |  | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | Moreover the circuit-breakers shall trip within the time corresponding to the test c of Table 7 when a current equal to 2,8 In is passed through all poles, the lower time limit being 0,1 s instead of 1 s, sec, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.2 | IS/IEC 60898-1 | 6 | N.A | N.A |  | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2 | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 9.12.12.2 | Verifications after the tests at reduced short-circuit currents, at 1 500 A and at service short-circuit capacity | Yes | Mandatory | The sample shown as number 1 in Table 23 is not subjected to the verification of this subclause, but it shall nevertheless comply with the requirements of 9.12.10. | Satisfactory or Not Satisfactory (endangered the operator or initiated a flashover between live conductive parts or between live conductive parts and earth or polyethylene foil shows holes or permanent arcing or no flashover between poles or between poles and frame or melting of the fuse F or fuse F') | Rated Voltage, Rated Current (In), No. of Poles, Rated short-circuit capacity (Icn), Type of Enclosures | Cl.9.12.12.2 | IS/IEC 60898-1 | 7 | N.A | N.A | [5 empty] | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Mechanical shock | Yes | Mandatory | With the circuit-breaker in the closed position, but not connected to any electrical source, the platform is lifted at its free end and then allowed to fall 50 times from a height of 40 mm, the interval between consecutive falls being such that the sample is allowed to come to rest. Before each change of position, the circuit-breaker is manually opened and closed. | Satisfactory or Not Satisfactory (circuit breaker opened) | Method of mounting | Cl.9.13.1.2 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Mechanical shock | Yes | Mandatory | The circuit-breaker is then secured to the opposite side of the vertical board C and the platform is allowed to fall 50 times as before. Before each change of position, the circuit-breaker is manually opened and closed. | Satisfactory or Not Satisfactory (circuit breaker opened) | Method of mounting | Cl.9.13.1.2 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Mechanical shock | Yes | Mandatory | After this test, the vertical board is turned through 90° about its vertical axis and, if necessary, repositioned so that the vertical axis of symmetry of the circuit-breaker is 200 mm from the hinge. Before each change of position, the circuit-breaker is manually opened and closed. | Satisfactory or Not Satisfactory (circuit breaker opened) | Method of mounting | Cl.9.13.1.2 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Mechanical shock | Yes | Mandatory | The platform is then allowed to fall 50 times as before, with the circuit-breaker on one side of the vertical board, and 50 times with the circuit-breaker on the opposite side. | Satisfactory or Not Satisfactory (circuit breaker opened) | Method of mounting | Cl.9.13.1.2 | IS/IEC 60898-1 | 4 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Resistance to mechanical stresses and impact | Yes | Mandatory | Surface-type circuit-breakers; Each circuit-breaker is subjected to ten blows, two of them being applied to the operating means and the remainder being evenly distributed over the parts of the sample likely to be subjected to impacts. | Satisfactory or Not Satisfactory (samples shows damage or covers broken making live parts accessible or impair the further use of the circuit-breaker, or operating means, linings and barriers of insulating material and the like, shows such damage) | Method of mounting | Cl.9.13.2.2 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Resistance to mechanical stresses and impact | Yes | Mandatory | Flush-type circuit-breakers; Each circuit-breaker is subjected to ten blows, two of them being applied to the operating means and the remainder being evenly distributed over the parts of the sample likely to be subjected to impacts. | Satisfactory or Not Satisfactory (samples shows damage or covers broken making live parts accessible or impair the further use of the circuit-breaker, or operating means, linings and barriers of insulating material and the like, shows such damage) | Method of mounting | Cl.9.13.2.2 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Resistance to mechanical stresses and impact | Yes | Mandatory | Panel board type circuit-breakers; Each circuit-breaker is subjected to ten blows, two of them being applied to the operating means and the remainder being evenly distributed over the parts of the sample likely to be subjected to impacts. | Satisfactory or Not Satisfactory (samples shows damage or covers broken making live parts accessible or impair the further use of the circuit-breaker, or operating means, linings and barriers of insulating material and the like, shows such damage) | Method of mounting | Cl.9.13.2.2 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Resistance to mechanical stresses and impact | Yes | Mandatory | Plug-in type circuit-breakers; Each circuit-breaker is subjected to ten blows, two of them being applied to the operating means and the remainder being evenly distributed over the parts of the sample likely to be subjected to impacts. | Satisfactory or Not Satisfactory (samples shows damage or covers broken making live parts accessible or impair the further use of the circuit-breaker, or operating means, linings and barriers of insulating material and the like, shows such damage) | Method of mounting | Cl.9.13.2.2 | IS/IEC 60898-1 | 4 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Resistance to mechanical stresses and impact | Yes | Mandatory | Screw-in type circuit-breakers; Each circuit-breaker is subjected to ten blows, two of them being applied to the operating means and the remainder being evenly distributed over the parts of the sample likely to be subjected to impacts. | Satisfactory or Not Satisfactory (samples shows damage or covers broken making live parts accessible or impair the further use of the circuit-breaker, or operating means, linings and barriers of insulating material and the like, shows such damage) | Method of mounting | Cl.9.13.2.2 | IS/IEC 60898-1 | 5 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Resistance to mechanical stresses and impact | Yes | Mandatory | Circuit-breakers for screw fixing ; Each circuit-breaker is subjected to ten blows, two of them being applied to the operating means and the remainder being evenly distributed over the parts of the sample likely to be subjected to impacts. | Satisfactory or Not Satisfactory (samples shows damage or covers broken making live parts accessible or impair the further use of the circuit-breaker, or operating means, linings and barriers of insulating material and the like, shows such damage) | Method of mounting | Cl.9.13.2.2 | IS/IEC 60898-1 | 6 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Resistance to mechanical stresses and impact | Yes | Mandatory | Circuit-breakers for rail mounting; Each circuit-breaker is subjected to ten blows, two of them being applied to the operating means and the remainder being evenly distributed over the parts of the sample likely to be subjected to impacts. | Satisfactory or Not Satisfactory (samples shows damage or covers broken making live parts accessible or impair the further use of the circuit-breaker, or operating means, linings and barriers of insulating material and the like, shows such damage) | Method of mounting | Cl.9.13.2.2 | IS/IEC 60898-1 | 7 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical shock and impact - Resistance to mechanical stresses and impact | Yes | Mandatory | Circuit-breakers intended both for screw fixing and for rail mounting ; Each circuit-breaker is subjected to ten blows, two of them being applied to the operating means and the remainder being evenly distributed over the parts of the sample likely to be subjected to impacts. | Satisfactory or Not Satisfactory (samples shows damage or covers broken making live parts accessible or impair the further use of the circuit-breaker, or operating means, linings and barriers of insulating material and the like, shows such damage) | Method of mounting | Cl.9.13.2.2 | IS/IEC 60898-1 | 8 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical stresses and impact - Screw-in type circuit-breakers | Yes | Mandatory | Screw-in type circuit-breakers are screwed home in an appropriate base, a torque of 2,5 Nm being applied for 1 min. | Satisfactory or Not Satisfactory (the sample shows damage impairing its further use) | Method of mounting | Cl.9.13.2.3 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical stresses and impact - circuit-breakers intended to be mounted on a rail | Yes | Mandatory | A downward vertical force of 50 N is applied without jerks for 1 min on the forward surface of the circuit-breaker, immediately followed by an upward vertical force of 50 N for 1 min | Satisfactory or Not Satisfactory (the circuit-breaker became loose or shows damage impairing its further use) | Method of mounting | Cl.9.13.2.4 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical stresses and impact - for all types of plug-in circuit-breakers designed for surface mounting; | Yes | Mandatory | A downward vertical force of 50 N is applied without jerks for 1 min on the forward surface of the circuit-breaker, immediately followed by an upward vertical force of 50 N for 1 min | Satisfactory or Not Satisfactory (the circuit-breaker became loose or shows damage impairing its further use) | Method of mounting | Cl.9.13.2.4 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.9 | Resistance to mechanical stresses and impact - plug-in type circuit-breakers | Yes | Mandatory | A force of 20 N is applied to the circuit-breaker portion at a point equidistant between the plug-in connections, without jerks for 1 min | Satisfactory or Not Satisfactory (the circuit-breaker became loose or moved from the base portion or shows damage impairing its further use) | Method of mounting | Cl.9.13.2.5 | IS/IEC 60898-1 |  | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.10 | Resistance to heat | Yes | Mandatory | The samples, without removable covers, if any, are kept for 1 h in a heating cabinet at a temperature of (100 ± 2) °C; | Satisfactory or Not Satisfactory (change impairing further use or sealing compound flow to such an extent that live parts got exposed) |  | Cl.9.4.1 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.10 | Resistance to heat | Yes | Mandatory | removable covers, if any, are kept for 1 h in the heating cabinet at a temperature of (70 ± 2) °C. | Satisfactory or Not Satisfactory (change impairing further use or sealing compound flow to such an extent that live parts got exposed) |  | Cl.9.4.1 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.10 | Resistance to heat | Yes | Mandatory | After the test and after the samples have been allowed to cool down to approximately room temperature, there shall be no access to live parts which are normally not accessible when the samples are mounted as for normal use, even if the standard test finger is applied with a force not exceeding 5 N. | Satisfactory or Not Satisfactory (access to live parts) |  | Cl.9.4.1 | IS/IEC 60898-1 | 3 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.10 | Resistance to heat | Yes | Mandatory | After the test, markings shall still be legible. | Satisfactory or Not Satisfactory (not legible) |  | Cl.9.4.1 | IS/IEC 60898-1 | 4 | N.A | N.A |  | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.10 | Resistance to heat | Yes | Mandatory | Ball pressure test where external circuit-breaker parts made of insulating material necessary to retain in position current-carrying parts and parts of the protective circuit, mm, Max | Number of decimal places - Value to be specified in Integers or whole numbers |  | Cl.9.4.2 | IS/IEC 60898-1 | 5 | N.A | N.A |  | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.10 | Resistance to heat | Yes | Mandatory | Ball pressure test where external circuit-breaker parts made of insulating material not necessary to retain in position current-carrying parts and parts of the protective circuit, mm, Max | Number of decimal places - Value to be specified in Integers or whole numbers |  | Cl.9.4.3 | IS/IEC 60898-1 | 6
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.11 | Resistance to abnormal heat and to fire | Yes | Mandatory | glow-wire test - for external parts of circuit-breakers made of insulating material necessary to retain in position current-carrying parts and parts of the protective circuit, by the test made at a temperature of (960 ± 15) °C; | Satisfactory or Not Satisfactory (there is visible flame and sustained glowing, or flames and glowing on the sample doesn't extinguish themselves within 30 s after the removal of the glow-wire or there is ignition of the tissue paper or scorching of the pinewood board) |  | - | IEC 60695-2-10 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.11 | Resistance to abnormal heat and to fire | Yes | Mandatory | glow-wire test - for all other external parts made of insulating material, by the test made at a temperature of (650 ± 10) °C. | Satisfactory or Not Satisfactory (there is visible flame and sustained glowing, or flames and glowing on the sample doesn't extinguish themselves within 30 s after the removal of the glow-wire or there is ignition of the tissue paper or scorching of the pinewood board) |  | - | IEC 60695-2-10 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.12 | Resistance to rusting | Yes | Mandatory | Ferrous parts shall be adequately protected against rusting. | Satisfactory or Not Satisfactory (signs of rust) |  | Cl.9.16 | IS/IEC 60898-1 | 1 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | 8.12 | Resistance to rusting | Yes | Mandatory | For small springs and the like and for inaccessible parts exposed to abrasion, a layer of grease may provide sufficient protection against rusting. Such parts are only subjected to the test if there is a doubt as to the effectiveness of the grease film, and in such a case the test is made without previous removal of the grease. | Satisfactory or Not Satisfactory (signs of rust) |  | Cl.9.16 | IS/IEC 60898-1 | 2 | N.A | N.A
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | 8.13 | Power loss | Yes | Mandatory | Power Loss, W, Max | Number of decimal places - Value upto 1 decimal places | Rated Current (In) | Cl.9.8.5 | IS/IEC 60898-1 | [32 empty] | - | 3 | - | 3.5 | - | 4.5 | - | 6 | - | 7.5 | - | 9 | - | 13 | - | 15 | - | 20
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | I.2 | Tripping tests (Routine) | Yes | Mandatory | Verification of the time-current characteristic - 1.13 In, sec, Min | Number of decimal places - Values upto 1 decimal place | Rated Current (In) | Cl.9.10.2.1 | IS/IEC 60898-1 | 1 |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | I.2 | Tripping tests (Routine) | Yes | Mandatory | Verification of the time-current characteristic - 1.45 In, sec, Max | Number of decimal places - Values upto 1 decimal place | Rated Current (In) | Cl.9.10.2.1 | IS/IEC 60898-1 | 2 |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2 |  |  |  |  | - | 1 | - | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | I.2 | Tripping tests (Routine) | Yes | Mandatory | Verification of the time-current characteristic - 2.55 In, sec, Max | Number of decimal places - Values upto 1 decimal place | Rated Current (In) | Cl.9.10.2.2 | IS/IEC 60898-1 | 3 | [7 empty] | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120 |  |  |  |  | 1 | 60 | 1 | 120
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | I.2 | Tripping tests (Routine) | Yes | Mandatory | Verification of the instantaneous tripping - No tripping, sec, Max | Number of decimal places - Values upto 1 decimal place | Type, Rated Current (In) | Cl.9.10.3.2, 9.10.3.3, 9.10.3.4 | IS/IEC 60898-1 | 1 |  |  |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | I.2 | Tripping tests (Routine) | Yes | Mandatory | Verification of the instantaneous tripping - tripping, sec, Max | Number of decimal places - Values upto 1 decimal place | Type, Rated Current (In) | Cl.9.10.3.2, 9.10.3.3, 9.10.3.4 | IS/IEC 60898-1 | 2 |  |  |  | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1 | - | 0.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | I.3 | Verification of clearances between open contacts (Routine) | Yes | Mandatory | No flashover or breakdown shall occur. | Satisfactory or Unsatisfactory (breakdown or flashover occured) | Type, Rated Current (In) | Cl.I.3 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.6 | Marking | Yes | Mandatory | Universal terminals: – no marking. | Satisfactory or Unsatisfactory (not marked) | Type of terminal | Cl.J.6 | IS/IEC 60898-1 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.6 | Marking | Yes | Mandatory | Non-universal terminals: terminals declared for rigid-solid conductors shall be marked by the letters "sol"; | Satisfactory or Unsatisfactory (not marked) | Type of terminal | Cl.J.6 | IS/IEC 60898-1 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.6 | Marking | Yes | Mandatory | Non-universal terminals: terminals declared for rigid (solid and stranded) conductors shall be marked by the letter "r"; | Satisfactory or Unsatisfactory (not marked) | Type of terminal | Cl.J.6 | IS/IEC 60898-1 | 3
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.6 | Marking | Yes | Mandatory | Non-universal terminals: terminals declared for flexible conductors shall be marked by the letter "f". | Satisfactory or Unsatisfactory (not marked) | Type of terminal | Cl.J.6 | IS/IEC 60898-1 | 4
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.6 | Marking | Yes | Mandatory | An appropriate marking indicating the length of insulation to be removed before insertion of the conductor into the terminal shall be shown on the circuit-breaker. | Satisfactory or Unsatisfactory (not marked) | Type of terminal | Cl.J.6 | IS/IEC 60898-1 | 5
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.6 | Marking | Yes | Mandatory | The manufacturer shall also provide information, in his literature, on the maximum number of conductors which may be clamped. | Satisfactory or Unsatisfactory (not marked) | Type of terminal | Cl.J.6 | IS/IEC 60898-1 | 6
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.1 | Connection or disconnection of conductors | Yes | Mandatory | Reliability of screwless system | Satisfactory or Unsatisfactory (terminal shall damaged in such a way as to impair its further use) | Rated Current (In), Type of terminal | Cl.J.9.1.1 | IS/IEC 60898-1 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.1 | Connection or disconnection of conductors | Yes | Mandatory | Test of reliability of connection | Satisfactory or Unsatisfactory (wire of the conductor escaped outside the terminal) | Rated Current (In), Type of terminal | Cl.J.9.1.2 | IS/IEC 60898-1 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.1 | Connection or disconnection of conductors | Yes | Mandatory | Tests of reliability of terminals for external conductors: mechanical strength | Satisfactory or Unsatisfactory ( conductor slipped out of the terminal) | Rated Current (In), Type of terminal | Cl.J.9.2 | IS/IEC 60898-1 | 3
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.2 | Dimensions of connectable conductors | Yes | Mandatory | Reliability of screwless system | Satisfactory or Unsatisfactory (terminal shall damaged in such a way as to impair its further use) | Rated Current (In), Type of terminal | Cl.J.9.1.1 | IS/IEC 60898-1 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.2 | Dimensions of connectable conductors | Yes | Mandatory | Test of reliability of connection | Satisfactory or Unsatisfactory (wire of the conductor escaped outside the terminal) | Rated Current (In), Type of terminal | Cl.J.9.1.2 | IS/IEC 60898-1 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.2 | Dimensions of connectable conductors | Yes | Mandatory | Tests of reliability of terminals for external conductors: mechanical strength | Satisfactory or Unsatisfactory ( conductor slipped out of the terminal) | Rated Current (In), Type of terminal | Cl.J.9.2 | IS/IEC 60898-1 | 3
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.3 | Connectable cross-sectional areas | Yes | Mandatory | Reliability of screwless system | Satisfactory or Unsatisfactory (terminal shall damaged in such a way as to impair its further use) | Rated Current (In), Type of terminal | Cl.J.9.1.1 | IS/IEC 60898-1 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.3 | Connectable cross-sectional areas | Yes | Mandatory | Test of reliability of connection | Satisfactory or Unsatisfactory (wire of the conductor escaped outside the terminal) | Rated Current (In), Type of terminal | Cl.J.9.1.2 | IS/IEC 60898-1 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.3 | Connectable cross-sectional areas | Yes | Mandatory | Tests of reliability of terminals for external conductors: mechanical strength | Satisfactory or Unsatisfactory ( conductor slipped out of the terminal) | Rated Current (In), Type of terminal | Cl.J.9.2 | IS/IEC 60898-1 | 3
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.4 | Insertion and disconnection of conductors | Yes | Mandatory | The insertion and disconnection of the conductors shall be made in accordance with the manufacturer’s instructions. | Satisfactory or Unsatisfactory | Type of terminal | Cl.J.8.4 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.5 | Design and construction of terminals | Yes | Mandatory | Terminals shall be so designed and constructed that: each conductor is clamped individually; | Satisfactory or Unsatisfactory (can't be clamped individually) | Type of terminal | J.8.5 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.5 | Design and construction of terminals | Yes | Mandatory | Terminals shall be so designed and constructed that: during the operation of connection or disconnection the conductors can be connected or disconnected either at the same time or separately; | Satisfactory or Unsatisfactory (can't be connected or disconnected either at the same time or separately) | Type of terminal | J.8.5 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.5 | Design and construction of terminals | Yes | Mandatory | Terminals shall be so designed and constructed that: inadequate insertion of the conductor is avoided. | Satisfactory or Unsatisfactory (inadequate insertion of the conductor) | Type of terminal | J.8.5 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.5 | Design and construction of terminals | Yes | Mandatory | It shall be possible to clamp securely any number of conductors up to the maximum provided for. | Satisfactory or Unsatisfactory (not possible to clamp securely any number of conductors up to the maximum provided for) | Type of terminal | J.8.5 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.5 | Design and construction of terminals | Yes | Mandatory | Reliability of screwless system | Satisfactory or Unsatisfactory (terminal shall damaged in such a way as to impair its further use) | Rated Current (In), type of terminal | Cl.J.9.1.1 | IS/IEC 60898-1 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.5 | Design and construction of terminals | Yes | Mandatory | Test of reliability of connection | Satisfactory or Unsatisfactory (wire of the conductor escaped outside the terminal) | Rated Current (In), type of terminal | Cl.J.9.1.2 | IS/IEC 60898-1 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.5 | Design and construction of terminals | Yes | Mandatory | Tests of reliability of terminals for external conductors: mechanical strength | Satisfactory or Unsatisfactory ( conductor slipped out of the terminal) | Rated Current (In), type of terminal | Cl.J.9.2 | IS/IEC 60898-1 | 3
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | J.8.6 | Resistance to ageing | Yes | Mandatory | Voltage drop, mV, Max | Number of decimal places – Value upto 1 decimal place | Rated Current (In), Type of terminals | Cl.J.9.3 | IS/IEC 60898-1 | 1 |  |  |  | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle | - | 22.5 or 1.5 times the value measured after the 24th cycle
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | J.8.6 | Resistance to ageing | Yes | Mandatory | After this test an inspection with the naked eye, by normal or corrected vision, without additional magnification, shall show no changes evidently impairing further use, such as cracks, deformations or the like. | Satisfactory or Unsatisfactory (cracked or deformed) | Rated Current (In), Type of terminals | Cl.J.9.3 | IS/IEC 60898-1 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | K.6 | Marking | Yes | Mandatory | The following information regarding the female connector according to IEC 61210 and the type of conductor to be used shall be given in the manufacturers' instructions: a) manufacturer’s name or trade mark; | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.K.6 | IS/IEC 60898-1 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | K.6 | Marking | Yes | Mandatory | The following information regarding the female connector according to IEC 61210 and the type of conductor to be used shall be given in the manufacturers' instructions: b) type reference; | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.K.6 | IS/IEC 60898-1 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | K.6 | Marking | Yes | Mandatory | The following information regarding the female connector according to IEC 61210 and the type of conductor to be used shall be given in the manufacturers' instructions: c) information on cross-sections of conductors and colour code of insulated female connectors (see Table K.1 below); | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.K.6 | IS/IEC 60898-1 | 3
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | K.6 | Marking | Yes | Mandatory | The following information regarding the female connector according to IEC 61210 and the type of conductor to be used shall be given in the manufacturers' instructions: d) the use of only silver or tin-plated copper alloys. | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.K.6 | IS/IEC 60898-1 | 4
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | K.8.1 | Clearances and creepage distances | Yes | Mandatory | the female connectors being fitted to the male tabs of the circuit breaker. | Satisfactory or Unsatisfactory | Type of terminals | Annex B | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | K.8.2.1 | Terminals for external conductors | Yes | Mandatory | Male tabs and female connectors shall be of a metal having mechanical strength, electrical conductivity and resistance to corrosion adequate for their intended use. | Satisfactory or Unsatisfactory (mechanical strength, electrical conductivity and resistance to corrosion inadequate for their intended use) | Type of terminals | Cl.K.8.2.1 | IS/IEC 60898-1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, A, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 1 | [27 empty] | 0.7 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Hole, A, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 2 | [27 empty] | 0.5 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, B, mm, Min | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 3 | [27 empty] | 7.8 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Hole, B, mm, Min | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 4 | [27 empty] | 7.8 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, C, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 5 | [27 empty] | 0.77 | 0.84
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Hole, C, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 6 | [27 empty] | 0.77 | 0.84
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, D, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 7 | [27 empty] | 6.2 | 6.4
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Hole, D, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 8 | [27 empty] | 6.2 | 6.4
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, E, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 9 | [27 empty] | 3.6 | 4.1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Hole, E, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 10 | [27 empty] | 4.3 | 4.7
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, F, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 11 | [27 empty] | 1.6 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Hole, F, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 12 | [27 empty] | 1.6 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, J, degree | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 13 | [27 empty] | 8 | 12
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Hole, J, degree | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 14 | [27 empty] | 8 | 12
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, M, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 15 | [27 empty] | 2.2 | 2.5
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, N, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 16 | [27 empty] | 1.8 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, P, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 17 | [27 empty] | 0.7 | 1.8
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Hole, P, mm | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 18 | [27 empty] | 0.7 | 1.8
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Dimple, Q, mm, Min | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 19 | [27 empty] | 8.9 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the male tab, Hole, Q, mm, Min | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 20 | [27 empty] | 8.9 | -
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | K.8.2.2 | Terminals for external conductors | Yes | Mandatory | Dimensions of the female connector, B3, mm, Max | Number of decimal places – Value upto 1 decimal place | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | 21 | [27 empty] | - | 7.8
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | K.8.2.3 | Terminals for external conductors | Yes | Mandatory | Mechanical overload-force | Satisfactory or Unsatisfactory (tab or to the circuit-breaker in which the tab is integrated got damaged) | Type of terminals | Cl.K.8.2.2 | IS/IEC 60898-1 | [28 empty] | - | 3.5
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | L.6 | Marking | Yes | Mandatory | Marking for terminals - Copper only | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.L.6 | IS/IEC 60898-1 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | L.6 | Marking | Yes | Mandatory | Marking for terminals - Aluminium only | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.L.6 | IS/IEC 60898-1 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | L.6 | Marking | Yes | Mandatory | Marking for terminals - Aluminium and Copper | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.L.6 | IS/IEC 60898-1 | 3
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | L.6 | Marking | Yes | Mandatory | the number of conductors | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.L.6 | IS/IEC 60898-1 | 4
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | L.6 | Marking | Yes | Mandatory | the screw torque values (if different from Table 11) | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.L.6 | IS/IEC 60898-1 | 5
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | L.6 | Marking | Yes | Mandatory | the cross-sections | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.L.6 | IS/IEC 60898-1 | 6
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | L.6 | Marking | Yes | Mandatory | The manufacturer shall state in his catalogue that, for the clamping of an aluminium conductor the tightening torque shall be applied with appropriate means. | Satisfactory or Unsatisfactory (not marked) | Type of terminals | Cl.L.6 | IS/IEC 60898-1 | 7
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | L.8.1.5.2 | Terminals for external conductors | Yes | Mandatory | For the connection of aluminium conductors, circuit-breakers shall be provided with screw type terminals allowing the connection of conductors having nominal cross-sections as shown in Table L.2. - smallest cross section area | Satisfactory or Unsatisfactory (not able to make proper connection) | Type of terminals, Rated Current (In) | Cl.L.8.1.5.2 | IS/IEC 60898-1 | 1
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | L.8.1.5.2 | Terminals for external conductors | Yes | Mandatory | For the connection of aluminium conductors, circuit-breakers shall be provided with screw type terminals allowing the connection of conductors having nominal cross-sections as shown in Table L.2. - largest cross section area | Satisfactory or Unsatisfactory (not able to make proper connection) | Type of terminals, Rated Current (In) | Cl.L.8.1.5.2 | IS/IEC 60898-1 | 2
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | L.8.1.5.2 | Test of reliability of screws, current-carrying parts and connections | Yes | Mandatory | Terminals for the connection of aluminium conductors and terminals of aluminium for the connection of copper or aluminium conductors shall have mechanical strength adequate to withstand the tests of 9.4, with the test conductors tightened with the torque indicated in Table 11, or with the torque specified by the manufacturer, which shall never be lower than that specified in Table 11. | Satisfactory or Unsatisfactory (connections became loose or their electrical function impaired or the screwed connections worked loose or there is damage or enclosures is damaged) | Type of terminals, Rated Current (In) | Cl.9.4 | IS/IEC 60898-1 | 3
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | L.8.1.5.4 | Current cycling test | Yes | Mandatory | For each screw-type terminal - the temperature rise, K, Max | Number of decimal places - Value to be specified in Integers or whole numbers | Type of terminals, Rated Current (In) | Cl.L.9.2 | IS/IEC 60898-1 | [30 empty] | - | 110
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Quantitative | L.8.1.5.4 | Current cycling test | Yes | Mandatory | For each screw-type terminal - the stability factor Sf, degree | Number of decimal places - Value to be specified in Integers or whole numbers | Type of terminals, Rated Current (In) | Cl.L.9.2 | IS/IEC 60898-1 | 2 | [29 empty] | -10 | 10
60898 | Part - 1 | NA | 2015 | 0 | Electrical Accessories circuited-breakers for overcurrent protection for household and similar installations | Electrical | Qualitative | National Annex A | BIS CERTIFICATION MARKING | Yes | Mandatory | The product may also be marked with the Standard Mark. | Satisfactory or Unsatisfactory (not marked) |  | National Annex A | IS/IEC 60898-1

## IS 60898_1_0_2015_0_Test Reques
Annex-D
No. of Poles | Type | Rated Voltages (Volts) | Rated Current (Amps) | Rated Frequency (Hz) | Rated short circuit capacities (Amps) | Phase of the system | Rated impulse withstand voltage | Degree of protection | method of mounting | Method of fixation system | Type of terminals | Type of Enclosure | I2t characterstics | Type designation | Material Group | "[DATA]" is any other information of the product needed for carrying out some tests. This information can be qualitative or quantitative
single-pole circuit-breakers | B -type | 230 V | 6 Amps | 50 Hz | 1500 | Single-phase system with mid-point earthed | 2.5 kV | IP20 | surface-type; | circuit-breakers, the electrical connections of which are not associated with the mechanical mounting | circuit-breakers with screw-type terminals for external copper conductors | enclosed-type (not requiring an appropriate enclosure) | as declared | XXXX | Group I
two-pole-circuit-breakers with one protected pole | C - type | 230 V | 8 | 60 Hz | 3000 | Three-phase systems | 4 kV | other (IPXX) | flush-type | circuit-breakers, the electrical connections of which are associated with the mechanical mounting. | circuit-breakers with screwless type terminals for external copper conductors (universal terminal) | unenclosed-type (for use with an appropriate enclosure) |  |  | Group II
two-pole circuit-breakers with two protected poles | D - type | 120/240 V | 10 |  | 4500 |  |  |  | panel board type | plug-in type | circuit-breakers with screwless type terminals for external copper conductors (non-universal terminal) |  |  |  | Group IIIa
three-pole circuit-breakers with three protected pole |  | 230/400 V | 13 |  | 6000 |  |  |  |  | bolt-on type; | circuit-breakers with flat quick-connect terminals for external copper conductors
four-pole circuit-breakers with three protected pole |  | 230 V | 16 |  | 10000 |  |  |  |  | screw-in type | circuit-breakers with screw-type terminals for external aluminium conductors
four-pole circuit-breakers with four protected poles. |  | 400/240 V | 20 |  | 20000
|  | 120/240 V | 25
|  | 230 V | 32
|  | 400/240 V | 40
|  | 120/240 V | 50
|  | 400 V | 63
80
100
125