## IS 9798_0_2013_3
IS Number | Part | Section | Year | Number of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause / Table/ Annex Reference | Test Parameter Name | To be tested and/or reported by Lab (Yes/No) | Mandatory or Optional | Requirement (as per Indian Standard) - No specified values to be mentioned here | Test Result / Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference | Sample Quantity | Equipment | Remarks | Stage Type(Single stage) |  | Stage Type (Two stage) |  | End Connection - Quick coupling |  | End Connection - Threaded |  | End Connection - Non Threaded |  | Diaphragm |  | Valve pad |  | Seal
[21 empty] | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 4.1 | Material | NO | Mandatory | All component parts shall be manufactured from or be treated with materials compatible with LPG as well as be unaffected by chemical or thermal influences that may be encountered in normal use. | To be checked based on declaraton basis | Declaration of material to be given by the manufacturer | [5 empty] | Clause is applicable for manufacturers
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.1.1 | Material | YES | Mandatory | Brass parts shall not be susceptible to season cracking. | Satisfactory / Unsatisfactory (Cracks observed) |  | Clause 4.1.1 | IS 2305
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Chemical | Quantitative | 4.2 | Material | YES | Mandatory | The body and cover of all regulators of rated capacity upto1 000 l/h shall be manufactured from zinc base alloys by pressure die-casting. | Please refer to Test report of IS 742. | Material of the body to be declared | Clause 4.2 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.2.1 | Finish | YES | Mandatory | The body and the cover of the regulator shall be electroplated or chemically treated (surface passivated) and painted or powder coated so as to resist the effect of atmospheric conditions to which the pressure regulator is exposed during its working life. The type of finish shall be as agreed to between the manufacturer and the customer. | To be checked based on declaration basis (As declared / Declaration not provided) | Surface treatment and type of surface finishing shall be declared. | Clause 4.2.1 | IS 9798 | 1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.2.1 | Finish | YES | Mandatory | The surface finished components shall be subjected to test for corrosion resistance as per IS 5528. The evaluation of the finish shall be done as per the method given in 6 of IS 6009. | Satisfactory / Unsatisfactory (Corrosion observed) |  | IS 5528 | IS 5528,IS 6009 | 2
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.2.1 | Finish | YES | Mandatory | The painted or powder coated surfaces shall be tested for adhesion of paint by the method described in Annex B | Satisfactory / Unsatisfactory (More than 3% ripping observed) |  | Annex B | IS 9798 | 3
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 4.3 | Diaphragm Material | YES | Mandatory | The material of diaphragm shall be of synthetic rubber or other material equally suitable for the application and shall satisfy the following requirements. | To be checked based on declaration basis | Material of Diaphragm to be declared.
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 4.3.1 | Diaphragm Material | YES | Mandatory | The material shall be free from porosity, pits and foreign particles and shall have a smooth, non-tacky surface with minimum talc or bloom. | Satisfactory / Unsatisfactory (The material is not free from Porosity/ The material is not free from pits/ The material is not free from foreign particles/ The material does not have a smooth surface/ The material does not have a non- tacky surface/ The material has excessive talc / The material has excessive bloom) |  | Clause 4.3.1 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.3.2 | Diaphragm Material | YES | Mandatory | Change in IRHD value, IRHD, Max | Value to be reported in Integer |  | Method A | IS 3400 (PART4) | 1 |  |  |  |  | 10 |  | 10
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.3.2 | Diaphragm Material | YES | Mandatory | Change in IRHD value, IRHD, Max | Value to be reported in Integer |  | Method B | IS 3400 (PART4) | 2 |  |  |  |  | 10 |  | 10
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 4.3.3 | Diaphragm Material | YES | Mandatory | The material shall be capable of withstanding a clamping pressure of 490 kPa (5 kgf/cm2) | Satisfactory / Unsatisfactory (could not withstand clamping pressure) |  | Clause 4.3.3 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.3.4 | Diaphragm Material | YES | Mandatory | The material shall be such that when an assembled regulator is subjected to the test as specified in AnnexC, the diaphragm shall not pull out or burst at a pressure less than 275 kPa, unit of measurement - kPa, Min | Number of decimal places-report in whole number |  | Annex C | IS 9798 | 1 |  |  |  | 275 |  | 275
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.3.4 | Diaphragm Material | YES | Mandatory | The material shall be such that when an assembled regulator is subjected to the test as specified in AnnexC, the diaphragm shall not pull out or burst at a pressure less than 2.8 kgf/cm2., unit of measurement - kgf/cm2, Min | Number of decimal places-report upto 1 decimal place. |  | Annex C | IS 9798 | 2 |  |  |  | 2.8 |  | 2.8
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.3.5 | Diaphragm Material | YES | Mandatory | The material shall, after immersion in n-pentane or octet commercial LPG for 72 h, meet the appropriate requirements specified in Annex D. (Extractable percent), % | Value to be reported in Integer |  | Annex D | IS 9798 | 1 | [13 empty] | -15 | 5 |  |  | -12 | 5
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.3.5 | Diaphragm Material | YES | Mandatory | The material shall, after immersion in n-pentane or octet commercial LPG for 72 h, meet the appropriate requirements specified in Annex D. Absorbed percent percent), % | Value to be reported in Integer |  | Annex D | IS 9798 | 2 | [13 empty] | -10 | 10 |  |  | -9 | 10
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.3.5 | Diaphragm Material | YES | Mandatory | Changes in hardness, before and after the immersion shall not exceed 15 IRHD , IRHD | Value to be reported in Integer |  | Annex D | IS 9798 | 3 |  |  |  | -15 | 15 | -15 | 15
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 4.3.6 | Diaphragm Material | YES | Mandatory | The material shall be such that the flexibility of the diaphragm shall not be impaired after the samples of the same have recovered completely to ambient temperatures from cooling to-20°C | Satisfactory / Unsatisfactory (Flexibility of the diaphragm was impaired) |  | Clause 8.9 | IS 9798 | 1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 4.3.6 | Diaphragm Material | YES | Mandatory | The material shall be such that the flexibility of the diaphragm shall not be impaired after the samples of the same have recovered completely to ambient temperatures from heating to 65°C. | Satisfactory / Unsatisfactory (Flexibility of the diaphragm was impaired) |  | Clause 8.9 | IS 9798 | 2
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.3.6 | Diaphragm Material | YES | Mandatory | The delivery pressure shall not be less than 2.206 kN/m2 and not more than 3.923 kN/m2 , unit of measurement- kN/m2 | Number of decimal places-report upto 3 decimal place. |  | Clause 8.9.1 | IS 9798 | 3 |  |  |  | 2.206 | 3.923 | 2.206 | 3.923
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.3.6 | Diaphragm Material | YES | Mandatory | The delivery pressure shall not be less than 22.5 gf/cm2 and not more than40 gf/cm2 , unit of measurement- gf/cm2 | Number of decimal places-report upto 1 decimal place. |  | Clause 8.9.1 | IS 9798 | 4 |  |  |  | 22.5 | 40 | 22.5 | 40
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 4.3.6 | Diaphragm Material | YES | Mandatory | A regulator shall not chatter or vibrate while being tested at any flow or inlet pressure in the range prescribed for the performance tests or under condition simulating normal service. If chattering or vibration occurs, the test shall be repeated | Satisfactory / Unsatisfactory (Chattering observed in regulator after repeat test/ Vibration observed in regulator after repeat test) |  | Clause 8.9.2 | IS 9798 | 5
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.3.7 | Diaphragm Material | YES | Mandatory | The material shall have 25 percent max compression set, unit of measurement- % (Max) | Number of decimal places-report in whole number |  | Annex E | IS 9798 | [5 empty] | 25 |  | 25
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 4.4.1 | Valve Pad Material | YES | Mandatory | The valve pad material shall be free from porosity, pits and foreign particles and shall have a smooth non tacky surface with minimum talc or bloom. | Satisfactory / Unsatisfactory (The material is not free from Porosity/ The material is not free from pits/ The material is not free from foreign particles/ The material does not have a smooth surface/ The material does not have a non- tacky surface/ The material has excessive talc / The material has excessive bloom) |  | Clause 4.4.1 | IS 9798 | 1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.4.1 | Valve Pad Material | YES | Mandatory | The material shall have low cold flow | Satisfactory / Unsatisfactory (Material had high cold flow) |  | Annex E | IS 9798 | 2
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.4.1 | Valve Pad Material | YES | Mandatory | The material shall have low creep characteristics | Satisfactory / Unsatisfactory (Material had high creep characteristics) |  | Annex E | IS 9798 | 3
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.4.1 | Valve Pad Material | YES | Mandatory | The material shall have compression set as specified in 4.4.5, unit of measurement-% (Max) | Number of decimal places-report in whole number |  | Annex E | IS 9798 | 4 |  |  |  |  | 40 |  | 40
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.4.2 | Valve Pad Material | YES | Mandatory | The material shall, after immersion in n-pentane or octet commercial LPG for 72 h, meet the appropriate requirements specified in Annex D. (Extractable percent), % | Value to be reported in Integer |  | Annex D | IS 9798 | 1 | [15 empty] | -12 | 5
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.4.2 | Valve Pad Material | YES | Mandatory | The material shall, after immersion in n-pentane or octet commercial LPG for 72 h, meet the appropriate requirements specified in Annex D. Absorbed percent percent), % | Value to be reported in Integer |  | Annex D | IS 9798 | 2 | [15 empty] | -9 | 10
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.4.2 | Valve Pad Material | YES | Mandatory | After immersion in hydrocarbon test, change in hardness value observed before and after the test shall not exceed 15 IRHD, units of measurement- IRHD | Number of decimal places- To be reported in integer |  | Annex D | IS 9798 | 3 |  |  |  |  | 15 |  | 15
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.4.3 | Valve Pad Material | YES | Mandatory | The material shall not show change of more than 10 IRHD when subjected to ageing of 72 h at 70°C in accordance with the method prescribed in IS 3400 (Part 4), units of measurement- IRHD | Number of decimal places- To be reported in integer |  |  | IS 3400 (Part 4) | [5 empty] | 10 |  | 10
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 4.4.4 | Valve Pad Material | YES | Mandatory | The valve pad fitted in its housing shall be immersed in pentane or commercial LPG in vapour phase for 72 h after which the valve pad shall not show evidence of being forced out of position due to swelling or other cause. | Satisfactory / Unsatisfactory (The valve pad was forced out of position due to swelling) |  | Clause 4.4.4 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.4.5 | Valve Pad Material | YES | Mandatory | The material shall have 40 percent maximum compression set when subjected to compression set test in accordance with the method prescribed in Annex E., unit of measurement-%(Max) | Number of decimal places-report upto 1 decimal place. |  | Annex E | IS 9798 | [5 empty] | 40 |  | 40
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 4.5 | Seal | YES | Mandatory | The O ring and rubber component material shall be free from porosity, pits and foreign particles and shall have a smooth non tacky surface with minimum talc or bloom. | Satisfactory / Unsatisfactory (The material is not free from Porosity/ The material is not free from pits/ The material is not free from foreign particles/ The material does not have a smooth surface/ The material does not have a non- tacky surface/ The material has excessive talc / The material has excessive bloom) |  | Clause 4.4.1 | IS 9798 | 1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.5 | Seal | YES | Mandatory | The material shall have low cold flow | Satisfactory / Unsatisfactory (Material had high cold flow) |  | Annex E | IS 9798 | 2
[6 empty] | Mechanical | Quantitative | 4.5 | Seal | YES | Mandatory | The material shall have low creep characteristics | Satisfactory / Unsatisfactory (Material had high creep characteristics) |  | Annex E | IS 9798 | 3
[6 empty] | Mechanical | Quantitative | 4.5 | Seal | YES | Mandatory | The material shall have compression set as specified in 4.4.5, unit of measurement-% (Max) | Number of decimal places-report in whole number |  | Annex E | IS 9798 | 4 |  |  |  |  | 40 |  | 40
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.5 | Seal | YES | Mandatory | The material shall, after immersion in pentane or commercial LPG for 72 h, meet the appropriate requirements given in Annex D. After this test, change in hardness value observed before and after the test shall not exceed 15 IRHD, units of measurement- IRHD | Integer |  | Annex D | IS 9798:2014 | 5 |  |  |  |  | 15 |  | 15
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.5 | Seal | YES | Mandatory | The material shall not show change of more than 10 IRHD when subjected to ageing of 72 h at 70°C , units of measurement- IRHD | Integer |  |  | IS 3400(PART 4) | 6 |  |  |  |  | 10 |  | 10
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 4.5 | Seal | YES | Mandatory | The material shall have 40 percent maximum compression set when subjected to compression set test in accordance with the method prescribed in Annex E., unit of measurement-%(Max) | Number of decimal places-report upto 1 decimal place. |  | Annex E | IS 9798 | 7 |  |  |  |  | 40 |  | 40
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.2 | CONSTRUCTION AND WORKMANSHIP | YES | Mandatory | The regulator, including all the component parts, shall be mechanically strong, of sound construction and of high standard of workmanship and finish. | Satisfactory / Unsatisfactory (The regulator and component parts were not mechanically strong / The regulator and component parts were not of sound construction / The regulator and component parts were not of high standard of workmanship or finish) |  | Clause 5.2 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.3 | CONSTRUCTION AND WORKMANSHIP | YES | Mandatory | The components of a regulator shall be interchangeable with the corresponding components of any other regulator of the same model and size | Satisfactory / Unsatisfactory (Components of regulator were not interchangeable) |  | Clause 5.3 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.4 | Screw Thread | YES | Mandatory | Except for the screwed ends of regulators not fitted with inlet or outlet connectors, screw threads shall comply with the requirements of IS 554. | To be checked based on declaration basis. Please refer to Test report of IS 554 | Declaration rgarding type of screw thread, designation to be provided | Table 1 | IS 554 | 1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.4 | Screw Thread | YES | Mandatory | Except for the screwed ends of regulators not fitted with inlet or outlet connectors, screw threads shall comply with the requirements o IS 2643 | To be checked based on declaration basis. Please refer to Test report of IS 2643 | Declaration rgarding type of screw thread, designation to be provided | Table 1 | IS 2643 | 2
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.4 | Screw Thread | YES | Mandatory | Except for the screwed ends of regulators not fitted with inlet or outlet connectors, screw threads shall comply with the requirements of IS 4218 (Parts 1 to 4). | To be checked based on declaration basis. Please refer to Test report of IS 4218 | Declaration rgarding type of screw thread, designation to be provided |  | IS 4218 (Parts 1 to 4). | 3
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.5 | Inlet Connection | YES | Mandatory | Where screwed connections are not used, the inlet of the pressure regulator shall be cast integrally as an inseparable part of the body or so fixed that it cannot be separated without damaging the body. | Satisfactory / Unsatisfactory (The inlet of pressure regulator was not cast integrally as an inseparable part of the body) |  | Clause 5.5 | IS 9798 | 1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.5 | Inlet Connection | YES | Mandatory | The size and the profile of the inlet connection shall match the outlet end of the spring actuated self closing valve of LPG cylinder to achieve a leak proof coupled joint without use of a resilient packing or washer or gasket as a part of the regulator. | Satisfactory / Unsatisfactory (Size and profile of the inlet connection did not match with the outlet end of valve of LPG cylinder) |  | Clause 5.5 | IS 9798 | 2
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.5.1 | Inlet Connection | YES | Mandatory | The inlet connection shall be designed to withstand a minimum hydrostatic pressure of 1.5 times the saturated vapour pressure of the gas at 65°C subject to a minimum of 18 kgf/cm2 for 120s. | Satisfactory / Unsatisfactory (Did not withstand the pressure) | Declaration required regarding the composition of LPG to be filled and its saturated vapour pressure. | Clause 5.5.1 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.5.2 | Inlet Connection | YES | Mandatory | The inlet connection shall also be capable to withstand a minimum pneumatic pressure equivalent to the maximum vapour pressure specified in 3.1 at ambient temperature.’ | Satisfactory / Unsatisfactory (Did not withstand the pressure) |  | Clause 5.5.2 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 5.5.3 | Screwed Connections - Screw Threads | YES | Mandatory | Screwed ends – Where inlet or outlet connections are not fitted, the inlet and outlet of a regulator with screwed ends shall comply with the requirements of IS 2643 or IS 4218 (Part 3). | To be checked based on declaration basis | Declaration rgarding type of screw thread, designation to be provided | Table 1 (IS 2643) or IS 4218 (Part 3) | IS 2643 or IS 4218 (Part 3). | a |  |  | Two separate rows has not been made as the requirement says compliance to any one of the ISS. Hence option should be open to lab to enter the result as per the declaration provided by manufacturer.
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 5.5.3 | Screwed Connections - Inlet Connections | YES | Mandatory | Where used, any washer, connector and nut of a screwed inlet union shall comply with the applicable mating dimensions of IS 8737 | To be checked based on declaration basis | Declaration rgarding type of screw , designation to be provided as per Figure 1/2/3/5A/5B of IS 8737 | Clause 5.5.3 | IS 8737 | b
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.5.4 | Inlet Sealing Requirement (SC Valve) | YES | Mandatory | Inlet Sealing Requirement (SC Valve) | Satisfactory / Unsatisfactory (leakage observed) |  | Annex K | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.6.1 | Non-Threaded Outlet Connection | YES | Mandatory | For regulators for domestic service the outlet nozzle shall be horizontal cast integrally with the body. | Satisfactory / Unsatisfactory (Casting of outlet nozzle is not horizontal and integral with body) |  | Clause 5.6.1 | IS 9798 | 1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.6.1 | Non-Threaded Outlet Connection | YES | Mandatory | The nozzle shall be any of the two specified in Fig. 2A and Fig. 2B. The choice of type shall be as per the agreement between the manufacturer and the purchaser | To be checked based on declaration basis | Type of nozzle and respective figure to be mentioned . | FIG 2A/FIG 2B | IS 9798 | 2 |  |  | Two separate rows has not been made as the requirement says compliance to any one of the figures in ISS. Hence option should be open to lab to enter the result as per the declaration provided by manufacturer.
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.6.2 | Threaded Outlet Connection | YES | Optional | Threaded outlet connection shall be as per the agreement between the manufacturer and the purchaser subject to approval from statutory authority | To be checked based on declaration basis | Declaration and approved diagram to be provided. | Clause 5.6.2 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.7 | Body | YES | Mandatory | The body and cover shall be strong enough to withstand the stress of connecting the regulator to the cylinder valve or piping installation and to withstand normal stress imposed by service conditions, without developing leakage at joints, permanent deformation or other damage which might impair the serviceability of the regulator. | Satisfactory / Unsatisfactory (Leakage observed from joints/Permanent deformation observed which might impair the serviceability of the regulator/ Other damages observed which might impair the serviceability of the regulator) |  | Clause 5.7 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.8 | Vent | YES | Mandatory | The breather hole (air vent above diaphragm space) shall be of such size and at such location on the cover that, a) does not easily get clogged/blocked; | Satisfactory / Unsatisfactory (breather hole location/size can not prevent easy blocking/clogging) |  | Clause 5.8 | IS 9798 | a
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.8 | Vent | YES | Mandatory | The breather hole (air vent above diaphragm space) shall be of such size and at such location on the cover that, b) the accidental entry of foreign matter is minimized | Satisfactory / Unsatisfactory (breather hole location/size can not minimize entry of foreign matters) |  | Clause 5.8 | IS 9798 | b
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.8 | Vent | YES | Mandatory | The breather hole (air vent above diaphragm space) shall be of such size and at such location on the cover that, c) it would be difficult for an instrument inserted through the air vent hole to reach the diaphragm. | Satisfactory / Unsatisfactory (breather hole location/size can not prevent easy access to diaphragm) |  | Clause 5.8 | IS 9798 | c
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.9 | Excess Flow Valve | YES | Optional | The excess flow valve, if provided shall meet the requirements given in Annex F | Satisfactory / Unsatisfactory (interval between successive bubbles was observed to be less than 10 seconds) |  | Annex F | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.10.1 | Valve Pad Fitting | YES | Mandatory | A valve pad (resilient) shall be so retained without the use of adhesive that it cannot loosen or work out of position under service conditions. | Satisfactory / Unsatisfactory (valve pad loosened/worked out of position) |  | Clause 5.10.1 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.10.2 | Valve Pad Fitting | YES | Mandatory | The inlet orifice and the valve pad of the pressure regulator shall be protected by provision of a filter of suitable material compatible with LPG, of appropriate size of perforations that does not hamper flow of vapour but is yet effective against ingress of contaminating agents in the gas. Any acceptable arrangement meeting this requirement, as agreed to between the manufacturer and the purchaser is permitted | Satisfactory / Unsatisfactory (Filter for inlet orifice and valve pad was not effective against ingress of contaminating agents) | Design/digram of filter is to be provided | Clause 5.10.2 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.1 | Strength of the inlet connection/regulator assembly | YES | Mandatory | The fixing of the inlet connection on to the regulator body , whether it is of the threaded or non - threaded type or in one piece, shall withstand the following tests, under the conditions defined in 8.11 (see Table 1): a) A torque of at least 30 Nm in both directions; and | Satisfactory / Unsatisfactory (Could not withstand the torque applied) |  | Table 1,Table 3 | IS 9798 | a
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.1 | Strength of the inlet connection/regulator assembly | YES | Mandatory | The fixing of the inlet connection on to the regulator body , whether it is of the threaded or non - threaded type or in one piece, shall withstand the following tests, under the conditions defined in 8.11 (see Table 1): b) A tensile strength test of 2 000 N | Satisfactory / Unsatisfactory (Could not withstand the tensile load applied) |  | Table 1,Table 3 | IS 9798 | b
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.2 | Outlet connection: For non - threaded hose connection | YES | Mandatory | The fixing of the outlet connection on to the regulator body, whether it is of the threaded, or non-threaded type or in one piece, shall resist the following tests, under the conditions defined in 8.11 (see Table 2): a) For non - threaded hose connection : 1) A torque of at least 30 Nm in one direction (verification not required for freely rotating connection) , | Satisfactory / Unsatisfactory (Could not withstand the torque applied) |  | Clause 8.11 table 2 | IS 9798 | a.1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.2 | Outlet connection: For non - threaded hose connection | YES | Mandatory | The fixing of the outlet connection on to the regulator body, whether it is of the threaded, or non-threaded type or in one piece, shall resist the following tests, under the conditions defined in 8.11 (see Table 2): a) For non - threaded hose connection : 2) Bending moment of 10 Nm , and | Satisfactory / Unsatisfactory (Could not withstand the bending moment applied) |  | Clause 8.11 table 2 | IS 9798 | a.2
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.2 | Outlet connection: For non - threaded hose connection | YES | Mandatory | The fixing of the outlet connection on to the regulator body, whether it is of the threaded, or non-threaded type or in one piece, shall resist the following tests, under the conditions defined in 8.11 (see Table 2): a) For non - threaded hose connection : 3) A tensile strength test of 2 000 N. | Satisfactory / Unsatisfactory (Could not withstand the tensile load applied) |  | Clause 8.11 table 2 | IS 9798 | a.3
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.2 | Outlet connection:For threaded unions: | YES | Mandatory | The fixing of the outlet connection on to the regulator body, whether it is of the threaded, or non-threaded type or in one piece, shall resist the following tests, under the conditions defined in 8.11 (see Table 2): b) For threaded unions 1) A torque of at least 30Nm in both directions (verification not required for freely rotating connections) , Unit of measurment-N-m (Min) | Number of decimal places: report upto 1 decimal place. |  | Clause 8.11 table 2 | IS 9798 | b.1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.2 | Outlet connection:For threaded unions: | YES | Mandatory | The fixing of the outlet connection on to the regulator body, whether it is of the threaded, or non-threaded type or in one piece, shall resist the following tests, under the conditions defined in 8.11 (see Table 2): b) For threaded unions 2) A bending moment of 10 Nm , Unit of measurment-N-m (Min) | Satisfactory / Unsatisfactory (Could not withstand the torque applied) |  | Clause 8.11 table 2 | IS 9798 | b.2
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.2 | Outlet connection:For threaded unions: | YES | Mandatory | The fixing of the outlet connection on to the regulator body, whether it is of the threaded, or non-threaded type or in one piece, shall resist the following tests, under the conditions defined in 8.11 (see Table 2): b) For threaded unions 3) A tensile strength test of 2 000 N, Unit of measurment-N (Min) | Satisfactory / Unsatisfactory (Could not withstand the tensile load applied) |  | Clause 8.11 table 2 | IS 9798 | b.3
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 5.11.3 | Strength of the connnection/regulator assembly | YES | Mandatory | torque necessary for the rotation of the freely rotating connection ,Unit of measurment-N-m (Max) | Number of decimal places: report upto 1 decimal place. |  | Clause 5.11.3 | IS 9798 | [9 empty] | 0.5 |  | 0.5
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.4 | Strength of the connnection/regulator assembly | YES | Mandatory | No distortion or breakage shall be evident | Satisfactory / Unsatisfactory (distortion/breakage observed) |  | Clause 5.11.4 | IS 9798 | 1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.4 | Strength of the connnection/regulator assembly | YES | Mandatory | The regulators shall comply with the soundness test described in 6 after application of the forces. | Satisfactory / Unsatisfactory (Please refer to the test results of clause 6) |  | Clause 6 | IS 9798 | 2 |  |  | It is to be noted that the requirements of soundness test is already covered undder clause 6. Only it is to be ensured by the lab that soundness test is performed after the application of load/checking strength as per Clause 5.11.4. Hence requirements of Clause 6 are not repeated here.
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 5.11.4 | Strength of the connnection/regulator assembly | YES | Mandatory | A regulator shall be considered leak tight when tested in accordance with 6.2 and if the leakage rate does not exceed 4 N mm3/s (the symbol N indicates conversion to normal temperature and pressure conditions, NTP that is 760 mm of Hg and 20°C), mm3/s (Max) | Value to be specified in whole number |  | Clause 6.1 | IS 9798 | 3 |  |  |  |  | 4 |  | 4
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.4 | Strength of the connnection/regulator assembly | YES | Mandatory | The regulator shall be leak tight when tested pneumatically at a pressure of 0.490 kN/m2 (5 gf/cm2) below twice the nominal outlet pressure when fitted with a relief valve or 14.70 kN/m2 (150 gf/cm2) when not fitted with a relief valve, applied through the outlet connection of a fully assembled regulator and held for not less than 30 s and not more than 60 s after stability has been achieved. | Satisfactory / Unsatisfactory (leakage observed) |  | Clause 6.2 | IS 9798 | 4
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.4 | Strength of the connnection/regulator assembly | YES | Mandatory | Those parts of the regulator which are normally subjected to the full cylinder pressure shall be leak tight at a minimum hydrostatic pressure of 1.5 times the saturated vapour pressure of the gas at 65°C or minimum 18 kgf/cm2, whichever is greater for a period of 120s. | Satisfactory / Unsatisfactory (leakage observed) |  | Clause 6.3 | IS 9798 | 5
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.11.4 | Strength of the connnection/regulator assembly | YES | Mandatory | Those parts of the regulator which are normally subjected to the full cylinder pressure shall also be tested for soundness at a pressure of 1 666 kPa (17 kgf/cm2) for a period of not less than 30 s and not more than 60 s, after stability has been achieved. | Satisfactory / Unsatisfactory (cracks observed/leakage observed) |  | Clause 6.4 | IS 9798 | 6
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.12.1 | Strength of Regulator Assembly when Fitted onto a Cylinder Valve | YES | Mandatory | The regulators when installed as indicated in the installation instruction shall resist the following tests under the conditions defined in 8.11 (see Table 3): a) A torque in both directions, 1) of at least 20 Nm for non-threaded hose outlet connections (15 Nm for quick coupling connections); and | Satisfactory/ Unsatisfactory (Could not resist the torque applied) | Separate cylinder valves to be provided. Type of connection to be declared. | Clause 5.12.1 / Amendment 2 | IS 9798 | a (1)
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.12.1 | Strength of Regulator Assembly when Fitted onto a Cylinder Valve | YES | Mandatory | The regulators when installed as indicated in the installation instruction shall resist the following tests under the conditions defined in 8.11 (see Table 3): a) A torque in both directions, 2) of at least 30 Nm for threaded outlet connections. In addition, regulators with screwed unions intended to be vertically mounted onto the cylinder valve, shall resist a torque of at least 20 Nm in the regulator plane (15 Nm for quick coupling connections). | Satisfactory/ Unsatisfactory (Could not resist the torque applied) | Separate cylinder valves to be provided. Type of connection to be declared. | Clause 5.12.1 / Amendment 2 | IS 9798 | a (2)
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.12.1 | Strength of Regulator Assembly when Fitted onto a Cylinder Valve | YES | Mandatory | The regulators when installed as indicated in the installation instruction shall resist the following tests under the conditions defined in 8.11 (see Table 3): b) A bending moment created by a force of 400 N directed upwards and whose application point is at the base of the outlet connection | Satisfactory/ Unsatisfactory (Could not resist the bending moment applied) | Separate cylinder valves to be provided. Type of connection to be declared. | Clause 5.12.1 / Amendment 2 | IS 9798 | b
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.12.1 | Strength of Regulator Assembly when Fitted onto a Cylinder Valve | YES | Mandatory | The regulators when installed as indicated in the installation instruction shall resist the following tests under the conditions defined in 8.11 (see Table 3): c) A tensile strength test of 500 N, for quick coupling connections only. | Satisfactory/ Unsatisfactory (Could not withstand tensile load of 500 N) | Separate cylinder valves to be provided. Type of connection to be declared. | Clause 5.12.1 / Amendment 2 | IS 9798 | c
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.12.2 | Strength of Regulator Assembly when Fitted onto a Cylinder Valve | YES | Mandatory | The mechanical strength required shall be ensured for all the positions of fixing of the regulator (as indicated in the installation instructions) onto the cylinder. | Satisfactory / Unsatisfactory (mechanical strength is not adequate) | Separate cylinder valves to be provided. | Clause 5.12.2 / Amendment 2 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.12.3 | Strength of Regulator Assembly when Fitted onto a Cylinder Valve | YES | Mandatory | There shall be no distortion or breakage that could affect the safety of the regulator. | Satisfactory / Unsatisfactory (Distortion observed that could affect the safety of the regulator/ Breakage observed that could affect the safety of the regulator) |  | Clause 5.12.3/ Amendment 2,clause 6 | IS 9798 | 1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.12.3 | Strength of Regulator Assembly when Fitted onto a Cylinder Valve | YES | Mandatory | The regulator shall comply with the soundness test described in 6 after application of the forces | Satisfactory / Unsatisfactory (Please refer to the test results of clause 6) |  | Clause 5.12.3/ Amendment 2,clause 6 | IS 9798 | 2 |  |  | It is to be noted that the requirements of soundness test is already covered undder clause 6. Only it is to be ensured by the lab that soundness test is performed after the application of load/checking strength as per Clause 5.12.3. Hence requirements of Clause 6 are not repeated here.
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 5.12.3 | Soundness | YES | Mandatory | A regulator shall be considered leak tight when tested in accordance with 6.2 and if the leakage rate does not exceed 4 N mm3/s (the symbol N indicates conversion to normal temperature and pressure conditions, NTP that is 760 mm of Hg and 20°C), mm3/sec (Max) | Value to be specified in whole number |  | Clause 6.1 | IS 9798 | 1 |  |  |  |  | 4 |  | 4 |  | 4 |  | 4
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.12.3 | Soundness | YES | Mandatory | The regulator shall be leak tight when tested pneumatically at a pressure of 0.490 kN/m2 (5 gf/cm2) below twice the nominal outlet pressure when fitted with a relief valve or 14.70 kN/m2 (150 gf/cm2) when not fitted with a relief valve, applied through the outlet connection of a fully assembled regulator. | Satisfactory / Unsatisfactory (leakage observed) |  | Clause 6.2 | IS 9798 | 2
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.12.3 | Soundness | YES | Mandatory | Those parts of the regulator which are normally subjected to the full cylinder pressure shall be leak tight at a minimum hydrostatic pressure of 1.5 times the saturated vapour pressure of the gas at 65°C or minimum 18 kgf/cm2, whichever is greater for a period of 120s. | Satisfactory / Unsatisfactory (leakage observed) |  | Clause 6.3 | IS 9798 | 3
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 5.12.3 | Soundness | YES | Mandatory | Those parts of the regulator which are normally subjected to the full cylinder pressure shall also be tested for soundness at a pressure of 1 666 kPa (17 kgf/cm2) for a period of not less than 30 s and not more than 60 s, after stability has been achieved. | Satisfactory / Unsatisfactory (leakage observed) |  | Clause 6.4 | IS 9798 | 4
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 6.1 | Soundness | YES | Mandatory | A regulator shall be considered leak tight when tested in accordance with 6.2 and if the leakage rate does not exceed 4 N mm3/s (the symbol N indicates conversion to normal temperature and pressure conditions, NTP that is 760 mm of Hg and 20°C), mm3/sec (Max) | Value to be specified in Integer |  | Clause 6.1 | IS 9798 | [5 empty] | 4 |  | 4 |  | 4 |  | 4
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 6.2 | Soundness | YES | Mandatory | The regulator shall be leak tight when tested pneumatically at a pressure of 0.490 kN/m2 (5 gf/cm2) below twice the nominal outlet pressure when fitted with a relief valve or 14.70 kN/m2 (150 gf/cm2) when not fitted with a relief valve, applied through the outlet connection of a fully assembled regulator. | Satisfactory / Unsatisfactory (leakage observed) |  | Clause 6.2 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 6.3 | Soundness | YES | Mandatory | Those parts of the regulator which are normally subjected to the full cylinder pressure shall be leak tight at a minimum hydrostatic pressure of 1.5 times the saturated vapour pressure of the gas at 65°C or minimum 18 kgf/cm2, whichever is greater for a period of 120s. | Satisfactory / Unsatisfactory (leakage observed) |  | Clause 6.3 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 6.4 | Soundness | YES | Mandatory | Those parts of the regulator which are normally subjected to the full cylinder pressure shall also be tested for soundness at a pressure of 1 666 kPa (17 kgf/cm2) for a period of not less than 30 s and not more than 60 s, after stability has been achieved. | Satisfactory / Unsatisfactory (leakage observed) |  | Clause 6.4 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.2 | Chatter test | YES | Mandatory | A regulator when tested shall not chatter or vibrate while being tested for performance: | Satisfactory / Unsatisfactory (Chattering observed/vibration observed) |  | Clause 8.2 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.9.1 | Performance test | YES | Mandatory | On gas flow rate of 10 to 100 percent of rated capacity, the delivery pressure shall not be less than 2.206 kN/m2 and not more than 3.923 kN/m2 , kN/m2 | Value to be specified upto 3 decimal place |  | Clause 8.9.1 | IS 9798 | 1 |  |  |  | 2.206 | 3.923 | 2.206 | 3.923
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.9.1 | Performance test | YES | Mandatory | On gas flow rate of 10 to 100 percent of rated capacity, the delivery pressure shall not be less than 22.5 gf/cm2 and not more than 40 gf/cm2 , gf/cm2 | Value to be specified upto 1 decimal place |  | Clause 8.9.1 | IS 9798 | 2 |  |  |  | 22.5 | 40 | 22.5 | 40
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.9.1 | Performance test | YES | Mandatory | Static (look up) pressure shall not exceed 4.41 kN/m2 (45 gf/cm2 or 450 mm of WC), kN/m2 (Max) | Value to be specified upto 2 decimal place |  | Clause 8.9.1 | IS 9798 | 3 |  |  |  |  | 4.41 |  | 4.41
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.9.2 | Performance test | YES | Mandatory | A regulator shall not chatter or vibrate while being tested at any flow or inlet pressure in the range prescribed for the performance tests or under condition simulating normal service. If chattering or vibration occurs, the test shall be repeated | Satisfactory / Unsatisfactory (Chattering observed/vibration observed) |  | Clause 8.9.2 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.1 | Performance test (Excess flow check valve) | YES | Mandatory | The excess flow check valve shall shut-off the gas flow in all the cases of disconnection of the flexible hose or tube fitted down stream of the regulator. | Satisfactory / Unsatisfactory (leakage observed) |  | Annex F | IS 9798 | 1
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.1 | Performance test (Excess flow check valve) | YES | Mandatory | This device shall operate for an increase in the rate between 120 percent and 200 percent of the rated capacity of the regulator at an angle of ±10° relative to its axis in the fixing position(s) of the regulator in the range and the rate obtained on hose or tube disconnections of minimum (–20°C) and maximum temperature (+65°C) condition | Satisfactory / Unsatisfactory (device malfunctioned) |  | Annex F | IS 9798 | 2
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.1 | Performance test (Excess flow check valve) | YES | Mandatory | For manual resetting devices a maximum residual leak of 15cm³/h is permitted, cm3/h (Max) | Value to be reported in whole number | Type of resetting device to be declared (manual/automatic) | Annex F | IS 9798 | 3 |  |  | Test is applicable only to manual resetting devices. Hence declaration is required.
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.1 | Performance test (Excess flow check valve) | YES | Mandatory | The regulator shall be subjected to full inlet pressure and examine the bubble indicator for the appearance of the bubbles. The interval between successive bubbles passing through it shall not be less than 10s. | Satisfactory / Unsatisfactory (interval between successive bubbles was observed to be less than 10 seconds) |  | Annex F | IS 9798 | 4
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.10.1 | Cycle Test | YES | Mandatory | When assessing a new design, a type approval test in accordance with Annex G shall be carried out. A fully assembled regulator shall withstand a minimum of 100 000 cycles of opening and closing operations, after which it shall be subjected to a soundness test as in 6.2, 6.3, 6.4 and performance as given in 8.9. | Satisfactory / Unsatisfactory (could not withstand required no of cycles of opening and closing) |  | Clause 8.9 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.1 | Performance test (After Cycle Test) | YES | Mandatory | On gas flow rate of 10 to 100 percent of rated capacity, the delivery pressure shall not be less than 2.206 kN/m2 and not more than 3.923 kN/m2 , kN/m2 | Value to be reported upto 3 decimal place |  | Clause 8.9.1 | IS 9798 | 1 |  |  |  | 2.206 | 3.923 | 2.206 | 3.923
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.1 | Performance test (After Cycle Test) | YES | Mandatory | On gas flow rate of 10 to 100 percent of rated capacity, the delivery pressure shall not be less than 22.5 gf/cm2 and not more than 40 gf/cm2, gf/cm2 | Value to be reported upto 1 decimal place |  | Clause 8.9.1 | IS 9798 | 2 |  |  |  | 22.5 | 40 | 22.5 | 40
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.1 | Performance test (After Cycle Test) | YES | Mandatory | Static (look up) pressure shall not exceed 4.41 kN/m2 , kN/m2 (Max) | Value to be reported upto 2 decimal place |  | Clause 8.9.1 | IS 9798 | 3 |  |  |  |  | 4.41 |  | 4.41
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.1 | Performance test (After Cycle Test) | YES | Mandatory | Static (look up) pressure shall not exceed 45 gf/cm2, gf/cm2 (Max) | Value to be reported upto 2 decimal place |  | Clause 8.9.1 | IS 9798 | 4 |  |  |  |  | 45 |  | 45
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.10.1 | Performance test (After Cycle Test) | YES | Mandatory | A regulator shall not chatter or vibrate while being tested at any flow or inlet pressure in the range prescribed for the performance tests or under condition simulating normal service. If chattering or vibration occurs, the test shall be repeated | Satisfactory / Unsatisfactory (Chattering observed / Vibration observed) |  | Clause 8.9.2 | IS 9798 | 5
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.10.2 | Low Temperature test | YES | Mandatory | The regulator is exposed to a temperature of –20°C for a minimum period of 10 min for the complete assembled unit to attain this temperature. It is then removed and left exposed to ambient conditions, after which it is tested. The method of carrying out the test shall be as per Annex H. If the regulator is fitted with excess flow check device, the performance of the excess flow check valve shall also be checked as per Annex F.Heating shall not be applied to reach the ambient temperature. | Satisfactory / Unsatisfactory (leakage observed) |  | Annex H | IS 9798 |  |  |  | Performance of flow check valve has already been covered under Clause 8.10
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.2.2 | Performance test (After Low Temperature Test) | YES | Mandatory | On gas flow rate of 10 to 100 percent of rated capacity, the delivery pressure shall not be less than 2.206 kN/m2 and not more than 3.923 kN/m2, kN/m2 | Value to be reported upto 3 decimal place |  | Clause 8.9.1 | IS 9798 | 1 |  |  |  | 2.206 | 3.923 | 2.206 | 3.923
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.2.2 | Performance test (After Low Temperature Test) | YES | Mandatory | On gas flow rate of 10 to 100 percent of rated capacity, the delivery pressure shall not be less than 22.5 gf/cm2 and not more than 40 gf/cm2 , gf/cm2 | Value to be reported upto 1 decimal place |  | Clause 8.9.1 | IS 9798 | 2 |  |  |  | 22.5 | 40 | 22.5 | 40
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.2.2 | Performance test (After Low Temperature Test) | YES | Mandatory | Static (look up) pressure shall not exceed 4.41 kN/m2 , kN/m2 (Max) | Value to be reported upto 2 decimal place |  | Clause 8.9.1 | IS 9798 | 3 |  |  |  |  | 4.41 |  | 4.41
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.2.2 | Performance test (After Low Temperature Test) | YES | Mandatory | Static (look up) pressure shall not exceed 45 gf/cm2 , gf/cm2 (Max) | Value to be reported in whole number |  | Clause 8.9.1 | IS 9798 | 4 |  |  |  |  | 45 |  | 45
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.10.2.2 | Performance test (After Low Temperature Test) | YES | Mandatory | A regulator shall not chatter or vibrate while being tested at any flow or inlet pressure in the range prescribed for the performance tests or under condition simulating normal service. If chattering or vibration occurs, the test shall be repeated | Satisfactory / Unsatisfactory (Chattering observed/vibration observed) |  | Clause 8.9.2 | IS 9798 | 5
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.3 | High-temp test | YES | Mandatory | The regulator is exposed to a temperature of 65°C for a minimum period of 10 min for the complete assembled unit to attain this temperature. It is then removed and left exposed to ambient conditions, after which it is tested. The method of carrying out the test shall be as per Annex H. If the regulator is fitted with excess flow check device, the performance of the excess flow check valve shall also be checked as per Annex F. | Satisfactory / Unsatisfactory (The interval between successive bubbles passing through is less than 10s) |  | Annex H & F | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.3.2 | Performance test (After High Temperature Test) | YES | Mandatory | On gas flow rate of 10 to 100 percent of rated capacity, the delivery pressure shall not be less than 2.206 kN/m2 and not more than 3.923 kN/m2, kN/m2 | Value to be reported upto 3 decimal place |  | Clause 8.9.1 | IS 9798 | 1 |  |  |  | 2.206 | 3.923 | 2.206 | 3.923
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.3.2 | Performance test (After High Temperature Test) | YES | Mandatory | On gas flow rate of 10 to 100 percent of rated capacity, the delivery pressure shall not be less than 22.5 gf/cm2 and not more than 40 gf/cm2 , gf/cm2 | Value to be reported upto 1 decimal place |  | Clause 8.9.1 | IS 9798 | 2 |  |  |  | 22.5 | 40 | 22.5 | 40
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.3.2 | Performance test (After High Temperature Test) | YES | Mandatory | Static (look up) pressure shall not exceed 4.41 kN/m2 , kN/m2 (Max) | Value to be reported upto 2 decimal place |  | Clause 8.9.1 | IS 9798 | 3 |  |  |  |  | 4.41 |  | 4.41
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Quantitative | 8.10.3.2 | Performance test (After High Temperature Test) | YES | Mandatory | Static (look up) pressure shall not exceed 45 gf/cm2 , gf/cm2 (Max) | Value to be reported in whole number |  | Clause 8.9.1 | IS 9798 | 4 |  |  |  |  | 45 |  | 45
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.10.3.2 | Performance test (After High Temperature Test) | YES | Mandatory | A regulator shall not chatter or vibrate while being tested at any flow or inlet pressure in the range prescribed for the performance tests or under condition simulating normal service. If chattering or vibration occurs, the test shall be repeated | Satisfactory / Unsatisfactory (Chattering observed/ Vibration observed) |  | Clause 8.9.2 | IS 9798 | 5
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.11.2 | Mechanical Strength of Connections (Regulator Intended to be Directly Connected to a Cylinder Valve) | YES | Mandatory | The points where the device is held and the test values are those shown in Tables 1/2/3. | Satisfactory / Unsatisfactory (Distortion observed /Damage observed/ Could not withstand the Force/torque) | Application of the regulator needs to be declared | Table 1, Table 2, Table 3 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.11.3 | Mechanical Strength of Connections (Devices with threaded connections) | YES | Mandatory | a) Devices with threaded connections, shall be mounted on the valve as indicated in the installation instructions (Force/Torque as per Table 3) | Satisfactory / Unsatisfactory (Distortion observed /Damage observed/ Could not withstand the Force/torque) | Type of connection (Threaded/quick coupling free rotating) to be declared | Table 3 | IS 9798 | a
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 8.11.3 | Mechanical Strength of Connections (Devices with free rotating quick coupling connections) | YES | Mandatory | b) Devices with free rotating quick coupling connection | Satisfactory / Unsatisfactory (Distortion observed /Damage observed/ Could not withstand the Force/torque) | Type of connection (Threaded/quick coupling free rotating) to be declared | Table 3 | IS 9798 | b
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 9.1 | Sealing | YES | Mandatory | If the regulator is permanently not crimped, the body and the cover of each regulator shall be sealed to discourage interference with the internal mechanism as well as the pressure setting. | Satisfactory / Unsatisfactory (body and cover not sealed) |  | Clause 9.1 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 9.1.1 | Sealing | YES | Mandatory | The manner of sealing shall be as agreed to between the purchaser and the manufacturer. | Satisfactory / Unsatisfactory (Manner of sealing is not as per declaration) | Manner of sealing for body and cover to be declared | Clause 9.1.1 | IS 9798
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 10.1 | Type test | NO | Mandatory | The following shall constitute type tests out of the various requirements: a) Diaphragm material (see 4.3); b) Valve pad material (see 4.4); c) Hydrostatic test (see 6.3); d) Low and high temperature tests (see 8.10.2 and see 8.10.3); e) Mechanical strength of connection (see 8.11); f) Tests for excess flow device, if provided (see 5.9) | [7 empty] | Classification of test is not a test requirement by itself. For test results please refer to relevant clauses.
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 10.2 | Routine tests | NO | Mandatory | The following shall be carried out as routine tests: a) Pneumatic test (see 6.2 and 6.4); and b) Chatter and performance test (see 8.9). | [7 empty] | Classification of test is not a test requirement by itself. For test results please refer to relevant clauses.
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 11.1 | Marking | YES | Mandatory | A Regulator shall be clearly and permanently marked with the following: a) Manufacturer’s name or trade-mark; | Marked/ Not Marked / Masked | Declaration of any marking other than Cl 11.1 to be given | Clause 11.1 | IS 9798 | a
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 11.1 | Marking | YES | Mandatory | A Regulator shall be clearly and permanently marked with the following: b) Month and year of manufacture | Marked/ Not Marked / Masked | Declaration of any marking other than Cl 11.1 to be given | Clause 11.1 | IS 9798 | b
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 11.1 | Marking | YES | Mandatory | A Regulator shall be clearly and permanently marked with the following: c) Rated capacity, in m3/h of LPG; | Marked/ Not Marked / Masked | Declaration of any marking other than Cl 11.1 to be given | Clause 11.1 | IS 9798 | c
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 11.1 | Marking | YES | Mandatory | A Regulator shall be clearly and permanently marked with the following: d) Number of this Indian Standard; and | Marked/ Not Marked / Masked | Declaration of any marking other than Cl 11.1 to be given | Clause 11.1 | IS 9798 | d
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 11.1 | Marking | YES | Mandatory | A Regulator shall be clearly and permanently marked with the following: e) Any other markings as agreed to between the purchaser and the manufacturer | Marked/ Not Marked / Masked | Declaration of any marking other than Cl 11.1 to be given | Clause 11.1 | IS 9798 | e
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 11.2.1 | BIS certification marking | NO | Mandatory | The use of Standard Mark is governed by the provisions of Bureau of Indian Standards Act, 1986 and the rules and Regulations made thereunder. The details of conditions under which the license for use of Standard Mark may be granted to manufacturers or producers may be obtained from the Bureau of Indian Standards. | Satisfactory/ Unsatisfactory (Not marked with BIS Standard Mark) |  | Clause 11.2.1 | IS 9798 |  |  |  | This clause is to be checked by IO while drawing sample. However during masking of CM/L No may be done by Sample Cell of laboratory (by painting or other means which does not affect the construction of regulator)
IS 9798 |  |  | 2013 | 3 | Low pressure regulators for use with LPG | Mechanical | Qualitative | 11.3 | BIS certification marking | NO | Mandatory | The markings may be distributed over the body, cover and sealing plate/cap as found convenient and as agreed to between the purchaser and the manufacturer | Satisfactory/ Unsatisfactory (Marking not as per the agreement between purchaser and the manufacturer) |  | Clause 11.3 | IS 9798 |  |  |  | This clause is to be checked by IO while drawing sample. However during masking of CM/L No may be done by Sample Cell of laboratory (by painting or other means which does not affect the construction of regulator)

## Test_Request_Format
Type | End Connection | Material grade | Surface treatment | Material of diaphragm | Thread designation | Composition of LPG | Mating Dimension | Type of Nozzle | Connection diagram approved drawing | Type of resetting device | Type of application | Marking | Manner of sealing
Single Stage | Quick Coupling
Threaded
Double Stage | Quick Coupling
Threaded
Chemically Treated
Painted
Powder coated
Zn Al 4
Zn Al 4 Cu 1
Synthetic rubber
Any other
Designation as per IS 554 or IS 2643 or IS 4218 (Parts 1 to 4).
Saturated vapour pressure of LPG
Figure 1/2/3/5A/5B of IS 8737
Figure 2A
Figuree 2B
Approved drawing from CCOE/PESO (including all components)
Manual
Automatic
To be directly connected
Threaded
Quick Coupling free rotating
Any other as per agreement
Any other as per agreement