## Test Report format IS 14772 202
Annex-C
IS Number | Part | Section | Year | Number of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause/ Table/ Annex Reference | Test Parameter Name | To be tested by Lab (YES / NO) | Mandatory or Optional | Characteristics (as per Indian Standard) - No specified values to be mentioned here | Test Result/ Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference | Sample Quantity | Equipment |  | Specified limits for Earthing Resistance | Specified limits for Earthing Resistance | Screw terminal connecting capacity | Screw terminal connecting capacity | enter from the upper part of any groove, hole or reverse taper | enter from the upper part of any groove, hole or reverse taper | Opening of a drain hole diameter in mm | Opening of a drain hole diameter in mm | Opening of a drain hole area in mm² | Opening of a drain hole area in mm² | Opening of a drain hole width or length in mm | Opening of a drain hole width or length in mm | Enclosure are surrounded by insulation in percent | Enclosure are surrounded by insulation in percent | flexible cable displaced in mm | flexible cable displaced in mm | flexible cable displaced in mm | flexible cable displaced in mm | specimen displaced | specimen displaced | displacement of the lever | displacement of the lever | Edge of the box displaced | Edge of the box displaced | Movement of the face of the box | Movement of the face of the box | Deflection of the face of the box | Deflection of the face of the box | Deflection of the box | Deflection of the box | Specified limits for Insulation Resistance | Specified limits for Insulation Resistance | permanent deformation at any point on the cover | permanent deformation at any point on the cover | Specified limits for diameter of the impression caused by the ball | Specified limits for diameter of the impression caused by the ball | Specified limits for Pull out of screws securing the crossbar to the box | Specified limits for Pull out of screws securing the crossbar to the box | Specified Limits for CREEPAGE DISTANCES, CLEARANCES AND DISTANCES For rated voltage ≤ 250 V | Specified Limits for CREEPAGE DISTANCES, CLEARANCES AND DISTANCES For rated voltage ≤ 250 V | Specified Limits for CREEPAGE DISTANCES, CLEARANCES AND DISTANCES For rated voltage > 250 and ≤ 440 V | Specified Limits for CREEPAGE DISTANCES, CLEARANCES AND DISTANCES For rated voltage > 250 and ≤ 440 V | Specified Limits for CTI Value | Specified Limits for CTI Value | If the test is quantitative, the Min and Max value to be written after applying the tolerance given in the standard. If only upper and lower limit is given, mention ONLY Min or ONLY Max balue and leave the other cell blank. If the test is Qualitative, both Only Min column to be filled by the qualitiative requirement, the Max column to be left blank
THIS ROW TO BE LEFT BLANK | [16 empty] | To be only filled if the Column I and Column J are having same information and Column M is having different information | NOT TO BE FILLED |  |  | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 6.1 | RATINGS | Yes | Mandatory | The preferred values of the rated voltage of the integrated or incorporated connecting devices are 250 V and 400 V a.c. (Volt, ) | To be checked on the declaration basis | Rated Voltage | 6.1 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 6.2 | RATINGS | Yes | Mandatory | The standard rated connecting capacities are 0.5 mm2, 0.75 mm2, 1 mm2, 1.5 mm2, 2.5 mm2, 4 mm2, 6 mm2, 10 mm2, 16 mm2, 25 mm2, 35 mm2. (mm2, ) | upto 2 decimal digit | rated connecting capacities | 6.2 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.1, Table 1 | CLASSIFICATION | Yes | Mandatory | The Nature of their Material: 7.1.1 Insulating | To be checked on the declaration basis | Insulating | 7.1, Table 1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.1, Table 1 | CLASSIFICATION | Yes | Mandatory | The Nature of their Material: 7.1.2 Metallic | To be checked on the declaration basis | Metallic | 7.1, Table 1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.1, Table 1 | CLASSIFICATION | Yes | Mandatory | The Nature of their Material: 7.1.3 Composite | To be checked on the declaration basis | Composite | 7.1, Table 1 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.1, Table 1 | CLASSIFICATION | Yes | Mandatory | The Nature of their Material: 7.1.4 Natural or Synthetic Rubber or a Mixture of both | To be checked on the declaration basis | Natural or Synthetic Rubber or a Mixture of both | 7.1, Table 1 | IS 14772 | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.2, Table 1 | CLASSIFICATION | Yes | Mandatory | The Type of Installation: 7.2.1 Flush, Semi-flush in Solid Walls, Ceilings or Floors 7.2.1.1 Not suitable for installation into concrete | To be checked on the declaration basis | Not suitable for installation into concrete | 7.2, Table 1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.2, Table 1 | CLASSIFICATION | Yes | Mandatory | 7.2.1 Flush, Semi-flush in Solid Walls, Ceilings or Floors : 7.2.1.2 Suitable for installation into concrete with a maximum temperature during the casting Process of +60 °C | To be checked on the declaration basis | Suitable for installation into concrete with a maximum temperature during the casting Process of +60 °C | 7.2, Table 1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.2, Table 1 | CLASSIFICATION | Yes | Mandatory | 7.2.1 Flush, Semi-flush in Solid Walls, Ceilings or Floors : 7.2.1.3 Suitable for installation into concrete with a maximum temperature during the casting process of +90 °C | To be checked on the declaration basis | Suitable for installation into concrete with a maximum temperature during the casting process of +90 °C | 7.2, Table 1 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.2, Table 1 | CLASSIFICATION | Yes | Mandatory | 7.2.2 Flush or Semi-flush in Hollow Walls, Hollow Ceilings, Hollow Floors or Furniture 7.2.2.1 Class Ha | To be checked on the declaration basis | Class Ha | 7.2, Table 1 | IS 14772 | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.2, Table 1 | CLASSIFICATION | Yes | Mandatory | 7.2.2 Flush or Semi-flush in Hollow Walls, Hollow Ceilings, Hollow Floors or Furniture : 7.2.2.2 Class Hb for walls | To be checked on the declaration basis | Class Hb for walls | 7.2, Table 1 | IS 14772 | 5
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.2, Table 1 | CLASSIFICATION | Yes | Mandatory | 7.2.2 Flush or Semi-flush in Hollow Walls, Hollow Ceilings, Hollow Floors or Furniture : 7.2.2.3 Class Hb for ceilings | To be checked on the declaration basis | Class Hb for ceilings | 7.2, Table 1 | IS 14772 | 6
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.2, Table 1 | CLASSIFICATION | Yes | Mandatory | 7.2.3 Surface Mounting on Walls, Ceilings, Floors or Furniture | To be checked on the declaration basis | Surface Mounting on Walls, Ceilings, Floors or Furniture | 7.2, Table 1 | IS 14772 | 7
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.3, Table 1 | CLASSIFICATION | Yes | Mandatory | The Type (s) of Inlets (Outlets)a 7.3.1 With Inlets for Sheathed Cables for Fixed Installations | To be checked on the declaration basis | With Inlets for Sheathed Cables for Fixed Installations | 7.3, Table 1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.3, Table 1 | CLASSIFICATION | Yes | Mandatory | The Type (s) of Inlets (Outlets)a : 7.3.2 With Inlets for Flexible Cables | To be checked on the declaration basis | With Inlets for Flexible Cables | 7.3, Table 1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.3, Table 1 | CLASSIFICATION | Yes | Mandatory | The Type (s) of Inlets (Outlets)a : 7.3.3 With Inlets for Plain Or corrugated Conduits | To be checked on the declaration basis | With Inlets for Plain Or corrugated Conduits | 7.3, Table 1 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.3, Table 1 | CLASSIFICATION | Yes | Mandatory | The Type (s) of Inlets (Outlets)a : 7.3.4 With Inlets for Threaded Conduits | To be checked on the declaration basis | With Inlets for Threaded Conduits | 7.3, Table 1 | IS 14772 | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.3, Table 1 | CLASSIFICATION | Yes | Mandatory | The Type (s) of Inlets (Outlets)a : 7.3.5 With Inlets for Other Types of Conductors/Cables or Conduits | To be checked on the declaration basis | With Inlets for Other Types of | 7.3, Table 1 | IS 14772 | 5
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.3, Table 1 | CLASSIFICATION | Yes | Mandatory | The Type (s) of Inlets (Outlets)a : 7.3.6 With Spouts ( hub) | To be checked on the declaration basis | Conductors/Cables or Conduits | 7.3, Table 1 | IS 14772 | 6
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.3, Table 1 | CLASSIFICATION | Yes | Mandatory | The Type (s) of Inlets (Outlets)a : 7.3.7 Without Inlets — Inlet openings will be made during installation | To be checked on the declaration basis | Without Inlets — Inlet openings will be made during installation | 7.3, Table 1 | IS 14772 | 7
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.4, Table 1 | CLASSIFICATION | Yes | Mandatory | The Clamping Means: 7.4.1 With Cable Retention | To be checked on the declaration basis | With Cable Retention | 7.4, Table 1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.4, Table 1 | CLASSIFICATION | Yes | Mandatory | The Clamping Means: 7.4.2 With Cable Anchorage | To be checked on the declaration basis | With Cable Anchorage | 7.4, Table 1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.4, Table 1 | CLASSIFICATION | Yes | Mandatory | The Clamping Means: 7.4.3 With Clamping Means for Flexible Conduit | To be checked on the declaration basis | With Clamping Means for Flexible Conduit | 7.4, Table 1 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.4, Table 1 | CLASSIFICATION | Yes | Mandatory | The Clamping Means: 7.4.4 Without Clamping Means | To be checked on the declaration basis | Without Clamping Means | 7.4, Table 1 | IS 14772 | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.5, Table 1 | CLASSIFICATION | Yes | Mandatory | The Minimum Temperature during installation : 7.5.1 –5 °C | To be checked on the declaration basis | –5 °C | 7.5, Table 1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.5, Table 1 | CLASSIFICATION | Yes | Mandatory | The Minimum Temperature during installation : 7.5.2 –15 °C | To be checked on the declaration basis | –15 °C | 7.5, Table 1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.5, Table 1 | CLASSIFICATION | Yes | Mandatory | The Minimum Temperature during installation : 7.5.3 –25 °C | To be checked on the declaration basis | –25 °C | 7.5, Table 1 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.6, Table 1 | CLASSIFICATION | Yes | Mandatory | 7.6 The degree of protection against access to hazardous parts and against harmful effects due to the ingress of solid foreign objects according to IS/IEC 60529 with a minimum degree of IP2X | To be checked on the declaration basis | The degree of protection against access to hazardous parts and against harmful effects due to the ingress of solid foreign objects | 7.6, Table 1 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.7, Table 1 | CLASSIFICATION | Yes | Mandatory | The degree of protection against harmful effects due to the ingress of water according to IS/IEC 60529 | To be checked on the declaration basis | The degree of protection against harmful effects due to the ingress of water according to IS/IEC 60529 | 7.7, Table 1 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.8, Table 1 | CLASSIFICATION | Yes | Mandatory | The degree of protection of the part mounted inside the hollow walls of the boxes classified according to 7.2.2.1 : 7.8.1 IP2X | To be checked on the declaration basis | IP2X | 7.8, Table 1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.8, Table 1 | CLASSIFICATION | Yes | Mandatory | The degree of protection of the part mounted inside the hollow walls of the boxes classified according to 7.2.2.1 : 7.8.2 > IP2X | To be checked on the declaration basis | > IP2X | 7.8, Table 1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.9, Table 1 | CLASSIFICATION | Yes | Mandatory | The provision for fixing accessories to boxes 7.9.1 Boxes Supplied with Screws | To be checked on the declaration basis | Boxes Supplied with Screws | 7.9, Table 1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.9, Table 1 | CLASSIFICATION | Yes | Mandatory | The provision for fixing accessories to boxes : 7.9.2 Boxes Intended to Receive Screws | To be checked on the declaration basis | Boxes Intended to Receive Screws | 7.9, Table 1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.9, Table 1 | CLASSIFICATION | Yes | Mandatory | The provision for fixing accessories to boxes : 7.9.3 Boxes Intended to Receive Claws | To be checked on the declaration basis | Boxes Intended to Receive Claws | 7.9, Table 1 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.9, Table 1 | CLASSIFICATION | Yes | Mandatory | The provision for fixing accessories to boxes : 7.9.4 Boxes Intended to Receive Other Means | To be checked on the declaration basis | Boxes Intended to Receive Other Means | 7.9, Table 1 | IS 14772 | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.10, Table 1 | CLASSIFICATION | Yes | Mandatory | The method of fixing the terminals or connecting devices in the connecting box : 7.10.1 With integrated clamping units | To be checked on the declaration basis | With integrated clamping units | 7.10, Table 1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.10, Table 1 | CLASSIFICATION | Yes | Mandatory | The method of fixing the terminals or connecting devices in the connecting box : 7.10.2 With incorporated terminals or connecting devices | To be checked on the declaration basis | With incorporated terminals or connecting devices | 7.10, Table 1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.10, Table 1 | CLASSIFICATION | Yes | Mandatory | The method of fixing the terminals or connecting devices in the connecting box : 7.10.3 With provisions for subsequent incorporation of terminals or connecting devices | To be checked on the declaration basis | With provisions for subsequent incorporation of terminals or connecting devices | 7.10, Table 1 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 7.10, Table 1 | CLASSIFICATION | Yes | Mandatory | The method of fixing the terminals or connecting devices in the connecting box : 7.10.4 Without fixing (for floating terminals or connecting devices) | To be checked on the declaration basis | Without fixing (for floating terminals or connecting devices) | 7.10, Table 1 | IS 14772 | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | Boxes and enclosures shall be marked with, the name, trademark or identification mark of the manufacturer or the responsible vendor | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | the first characteristic numeral for the degree of protection against access to hazardous parts and against harmful effects due to ingress of solid foreign objects, if declared to be higher than 4 in which case the second characteristic numeral shall malso be marked; | To be checked on the declaration basis | NA | 8.1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | the second characteristic numeral for the degree of protection against harmful effects due to ingress of water, if declared to be higher than 2 in which case the first characteristic numeral shall also be marked | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | The following marking IPXX on the cover of flush enclosures intended to be mounted on rough surfaces and where the IP is dependent on the surface (see Fig. 5). The IP code, if applicable, shall be marked on the outside of the enclosure so as to be easily discernible when the enclosure is mounted and wired as for normal use; | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | For boxes and enclosures classified as in 7.2.2.2 and 7.2.2.3, the minimum internal volume in cm3 as determined by the test in 12.16. The internal volume shall be marked on the inside of the box or enclosure. The marking on a box or enclosure shall be such that the value can be read after installation of the box in the normal manner but before the installation of the wiring devices and wiring; | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 5
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | The type reference, which may be a catalogue number | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 6
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | Plus 90°C for boxes and enclosures classified according to 7.2.1.3; | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 7
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | the necessary information concerning the openings which can be made during installation in the case of boxes and enclosures classified according to 7.3.7 | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 8
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | the minimum temperature during installation for boxes classified according to 7.5.2 and 7.5.3; | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 9
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | the first characteristic numeral for the degree of protection against access to hazardous parts and against harmful effects due to ingress of solid foreign objects, if declared to be higher than 4 in which case the second characteristic numeral shall also be marked; | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 10
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | the symbol Ha for boxes classified according to 7.2.2.1 and the symbol Hb for boxes classified according to 7.2.2.2 and 7.2.2.3 | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 11
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.1 | Marking | Yes | Mandatory | In special cases, in order to achieve a higher degree of protection by the use of special parts an instruction sheet should be provided and should indicate the higher degree of protection. In such a case, the marking covers the initial degree of protection | Satisfactory/Unsatisfactory/Masked | NA | 8.1 | IS 14772 | 12
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.2 | Durability of Marking | Yes | Mandatory | After the test, the marking shall still be legible | Satisfactory/Unsatisfactory- not legible | NA | 8.2 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.2 | Marking | Yes | Mandatory | The product(s) conforming to the requirements of this standard may be marked with BIS Certification Mark | Satisfactory/Unsatisfactory/Masked | NA | 8.2 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 8.3 | Marking | Yes | Mandatory | The product(s) conforming to the requirements of this standard may be certified as per the conformity assessment schemes under the provisions of the Bureau of Indian Standards Act, 2016 and the Rules and Regulations framed thereunder, and the products may be marked with the Standard Mark. | Satisfactory/Unsatisfactory/Masked | NA | 8.3 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 9.1 | Dimensions | Yes | Mandatory | Boxes and enclosures shall comply with the appropriate standard sheets, if any measurement | Satisfactory/Unsatisfactory | NA | 9.1 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 9.2 | Dimensions | Yes | Mandatory | Compliance is checked by inspection and measurement | Satisfactory/Unsatisfactory | NA | 9.2 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 10.1 | Protection Against Electric Shock | Yes | Mandatory | Boxes and enclosures shall be so designed that, when they are assembled, equipped and installed as for normal use in accordance with the manufacturer’s instructions, live parts are not accessible. | Satisfactory/Unsatisfactory (live parts are accessible) | NA | 10.1 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 10.2 | Protection Against Electric Shock | Yes | Mandatory | Where enclosures are supplied without a cover, cover-plate or an accessory they are tested with the appropriate parts fitted according to the information given in the manufacturer’s instructions. | Satisfactory/Unsatisfactory | NA | 10.2 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 10.3 | Protection Against Electric Shock | Yes | Mandatory | Compliance is checked by inspection and in case of doubt by the following test. | Satisfactory/Unsatisfactory | NA | 10.3 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 10.4 | Protection Against Electric Shock | Yes | Mandatory | Enclosures shall be tested with test probe 11 according to IS 1401 applied for 1 min with a force of 20 N, and the test probe shall not penetrate in the internal volume of the enclosure | Satisfactory/Unsatisfactory (The test probe penetrate in the Internal Volume of Enclosure/ The test probe penetrated in the Internal Volume of Enclosure) | NA | 10.4 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 10.5 | Protection Against Electric Shock | Yes | Mandatory | Tests shall be carried out on parts that are accessible after installation. | Satisfactory/Unsatisfactory | NA | 10.5 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 10.6 | Protection Against Electric Shock | Yes | Mandatory | In addition, all enclosures according to 7.1.1, 7.1.3 and 7.1.4 with parts made of thermoplastic or elastomeric material shall be subjected for 1 min to a force applied through the tip of test probe 11 of IS 1401 but at an ambient temperature of +(35 ± 2)°C, the enclosure being at this temperature, at a force of 75 N | Satisfactory/Unsatisfactory | NA | 10.6 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 10.7 | Protection Against Electric Shock | Yes | Mandatory | The probe is applied to all places where yielding of insulating material could impair the safety with a force of 75 N except to membranes, grommets and knock-outs or the like. | Satisfactory/Unsatisfactory | NA | 10.7 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 10.8 | Protection Against Electric Shock | Yes | Mandatory | Knock-outs are tested according to 12.9.2 | Satisfactory/Unsatisfactory | NA | 12.9.2 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 11.1 | Provision for Earthing : Boxes and Enclosures with Exposed Conductive Parts | Yes | Mandatory | Earthing Resistance (Ω, Maximum) | Ohm (upto 2 decimal digit) | NA | 11.1 | IS 14772 | 1 |  |  |  |  | 0.05
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 11.1 | Provision for Earthing: Boxes and Enclosures with Exposed Conductive Parts | Yes | Mandatory | The earthing means or the provision for the fitting of such an earthing means shall be located so that: a) the means is readily accessible through the open face of the box, b) the removal of an accessory mounted in the box does not disturb the continuity of the earthing circuit, and c) the means is not part of a removable cover, back, or side of the box or enclosure. | Satisfactory/Not Provided | NA | 11.1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 11.2 | Provision for Earthing: Boxes and Enclosures of Insulating Material Classified According to 7.2.2.2 and 7.2.2.3 | Yes | Mandatory | Boxes and enclosures of insulating material shall be provided with a minimum of one earthing strap | Satisfactory/Not Provided | NA | 11.2 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 11.2 | Provision for Earthing: Boxes and Enclosures of Insulating Material Classified According to 7.2.2.2 and 7.2.2.3 | Yes | Mandatory | Boxes and enclosures of insulating material shall be provided one earthing strap having one screw terminal for earthing purposes with a connecting capacity of at least 4 mm2. | Satisfactory/Unsatisfactory | NA | 11.2 | IS 14772 | 2 | [5 empty] | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 11.2 | Provision for Earthing: Boxes and Enclosures of Insulating Material Classified According to 7.2.2.2 and 7.2.2.3 | Yes | Mandatory | The design of the earthing strap shall ensure that the metal mounting yokes of accessories mounted inside the box and metallic covers mounted on the box are connected to the earthing conductors (see Fig. 3 and Fig. 4). | Satisfactory/Not Provided | NA | 11.2 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 11.2 | Provision for Earthing: Boxes and Enclosures of Insulating Material Classified According to 7.2.2.2 and 7.2.2.3 | Yes | Mandatory | The earthing strap shall be securely fastened to the box or enclosure. | Satisfactory/Unsatisfactory | NA | 11.2 | IS 14772 | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 11.3 | Provision for Earthing: Boxes or Enclosures with Removable Sides According to 7.1.2 | Yes | Mandatory | A box or enclosure classified according to 7.1.2 that has removable sides shall be constructed so that the electrical bond between separable parts includes at least one threaded screw connection. | Satisfactory/Unsatisfactory | NA | 11.3 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 11.4 | Provision for Earthing: Earthing Terminal Threads | Yes | Mandatory | The screws are tightened and loosened 5 times. The test is made by using a suitable screwdriver or an appropriate tool applying a torque as indicated in Table 4. During the test, there shall be no damage, such as breakage of screw or damage to the head slot (rendering the use of the appropriate screwdriver impossible) or to the threads or to then closure impairing the further use of the fixing means. The screws shall be gradually tightened in one smooth and continuous movement. | Satisfactory/Unsatisfactory | NA | 11.4 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.1 | CONSTRUCTION : General | Yes | Mandatory | Boxes and enclosures shall be constructed without sharp edges. Burrs shall be removed from mould lines of interior surfaces so that there are no sharp edges or undue obstructions to the passage of wiring or coupling of parts in the intended use of the product. | Satisfactory/Unsatisfactory | NA | 12.1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.1 | CONSTRUCTION : General | Yes | Mandatory | The inner and outer surfaces of a box or cover shall not be subject to peeling, scaling or flaking and shall be smooth and free from blisters, cracks, and other defects. Compliance is checked by inspection. | Satisfactory/Unsatisfactory | NA | 12.1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.1 | CONSTRUCTION : Lids, Covers or Cover-Plates or Parts of Them: General | Yes | Mandatory | Lids, covers, or cover-plates or parts of them, such as protective membranes, which are intended to ensure protection against electric shock, shall be held in place effectively. | Satisfactory/Unsatisfactory | NA | 12.2.1 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.2 | CONSTRUCTION : Lids, Covers or Cover-Plates or Parts of Them: Screw-type Fixing | Yes | Mandatory | A box or enclosure intended to accept a lid, cover, or cover plate by means of screw fixing shall be provided with means to accommodate the intended screws. | Satisfactory/Unsatisfactory | NA | 12.2.2 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.3.1 | CONSTRUCTION :Lids, Covers or Cover-Plates or Parts of Them: Non-screw-type Fixing Operable Without the Use of a Tool or a Key: General | Yes | Mandatory | A box or enclosure intended to accept a lid, cover, or cover plate with non-screw- type fixing operable without the use of a tool or a key shall be provided with means to fix the lid, cover, or cover plate. | Satisfactory/Unsatisfactory | NA | 12.2.3.1 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.3.2 | CONSTRUCTION : Lids, Covers or Cover-Plates or Parts of Them: Non-screw-type Fixing Operable Without the Use of a Tool or a Key: Verification of the non-removal of the lids, covers or cover-plates | Yes | Mandatory | Forces are gradually applied in one smooth and continuous movement in a direction perpendicular to the mounting surfaces, in such a way that the resulting force acting on the center of the lids, covers or cover plates, or parts of them, is as specified in the relevant column of Table 2. The force is applied for 1 min. The lids, covers or cover-plates, shall not come off. | Satisfactory/Unsatisfactory | NA | 12.2.3.2 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.3.2 | CONSTRUCTION : Lids, Covers or Cover-Plates or Parts of Them: Non-screw-type Fixing Operable Without the Use of a Tool or a Key: Verification of the non-removal of the lids, covers or cover-plates | Yes | Mandatory | For flush-mounting boxes or enclosures, the test is then repeated on new specimens, the lid, cover or cover- plate is mounted on the box, after a sheet of hard material (1 ± 0.1) mm thick, has been fitted on the wall around the supporting frame, as shown in Fig. 5. The sheet of hard material is used to simulate wallpaper and may consist of a number of pieces. | Satisfactory/Unsatisfactory | NA | 12.2.3.2 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.3.3 | CONSTRUCTION : Lids, Covers or Cover-Plates or Parts of Them: Non-screw-type Fixing Operable Without the Use of a Tool or a Key: Verification of the removal of the lids, covers or cover-plates | Yes | Mandatory | A force not exceeding that specified in the relevant column of Table 2 is gradually applied in one smooth and continuous movement, in a direction perpendicular to the mounting/supporting surfaces, to lids, covers or cover-plates, or parts of them by means of a hook placed in turn in each of the grooves, holes, spaces or the like, provided for removing them. The lids, covers or cover-plates shall come off. The test is made 10 times on each separable part the f ixing of which is not dependent on screws (equally distributing as far as practicable the application points); the removal force is applied each time to the different grooves, holes or the like provided for removing the separable part. | Satisfactory/Unsatisfactory | NA | 12.2.3.3 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.3.3 | CONSTRUCTION : Lids, Covers or Cover-Plates or Parts of Them: Non-screw-type Fixing Operable Without the Use of a Tool or a Key: Verification of the removal of the lids, covers or cover-plates | Yes | Mandatory | For flush-mounting boxes or enclosures, the test is then repeated on new specimens. The lid, cover or cover-plate is mounted on the box after a sheet of hard material (1 ± 0.1) mm thick has been fitted on the wall around the supporting frame, as shown in Fig. 5. After the test, the specimens shall show no damage within the meaning of this standard. | Satisfactory/Unsatisfactory | NA | 12.2.3.3 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.3.4 | CONSTRUCTION : Lids, Covers or Cover-Plates or Parts of Them: Non-screw-type Fixing Operable Without the Use of a Tool or a Key: Verification of the outline of lids, covers and cover-plates | Yes | Mandatory | In the case of a lid, cover or cover-plate fixed without screws to another lid, cover or cover-plate or to a mounting box, having the same outline dimensions, theface B of the gauge shall be placed at the same level as the junction; the outline of the lid, cover or cover-plate shall not exceed the outline of the supporting surface. | Satisfactory/Unsatisfactory | NA | 12.2.3.4 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.3.4 | CONSTRUCTION : Lids, Covers or Cover-Plates or Parts of Them: Non-screw-type Fixing Operable Without the Use of a Tool or a Key: Verification of the outline of lids, covers and cover-plates | Yes | Mandatory | The distances between the face C of the gauge and the outline of the side under test, measured parallel to face B, shall not decrease (with the exception of grooves, holes, reverse tapers or the like, placed at a distance less than 7 mm from a plane including face B and complying with the test of 12.2.3.5) when measurements are repeated starting from point X in the direction of the arrow Y (see Fig. 8). | Satisfactory/Unsatisfactory | NA | 12.2.3.4 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.3.5 | CONSTRUCTION : Lids, Covers or Cover-Plates or Parts of Them: Non-screw-type Fixing Operable Without the Use of a Tool or a Key: Verification of grooves, holes and reverse tapers | Yes | Mandatory | A gauge according to Fig. 9, applied with a force of (1 ± 0.2) N, shall not enter more than 1.0 mm from the upper part of any groove, hole or reverse taper or the like when the gauge is applied parallel to the mounting/ supporting surface and at right angles to the part under test, as shown in Fig. 10. | Satisfactory/Unsatisfactory | NA | 12.2.3.5 | IS 14772 | [9 empty] | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.2.4 | CONSTRUCTION : Lids, Covers or Cover-Plates or Parts of Them: Non-screw-type Fixing Operable Without the Use of a Tool or a Key: Non Screw-type Fixing Operable with the Use of a Tool or a Key | Yes | Mandatory | For lids, covers or cover-plates whose fixing is not dependent on screws and whose removal is obtained by using a tool and/or a key, in accordance with the manufacturer’s instructions, compliance is checked by the same tests of 12.2.3 except that the lids, covers or cover-plates or parts of them need not come off when applying a force not exceeding 120 N in directions perpendicular to the mounting/supporting surface. | Satisfactory/Unsatisfactory | NA | 12.2.4 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.3 | CONSTRUCTION : Drain Holes | Yes | Mandatory | Surface and semi-flush mounting enclosures with a degree of protection IPX1 to IPX6 shall be designed to allow the opening of a drain hole of at least 5 mm in diameter or 20 mm2 in area with a minimum width or length of 3 mm. (mm or mm² and mm, Minimum) | mm or mm² and mm(upto 2 decimal digit) | NA | 12.3 | IS 14772 | [10 empty] | 5 |  | 20 |  | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.3 | CONSTRUCTION : Drain Holes | Yes | Mandatory | Drain holes shall be so located and available in such a number that one of the holes can always become effective in any intended mounting position of the enclosure. | Satisfactory/Unsatisfactory | NA | 12.3 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.4 | CONSTRUCTION : Mounting of Enclosures | Yes | Mandatory | Enclosures shall have provisions for their suitable attachment according to the type of installation (see 7.2). | Satisfactory/Unsatisfactory | NA | 12.4 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.4 | CONSTRUCTION : Mounting of Enclosures | Yes | Mandatory | Enclosures of insulating material shall be constructed in such a way that any conductive parts of fixing means inside the box or enclosure intended to be used for mounting the enclosure are surrounded by insulation which projects above the top of the fixing means by an amount of not less than 10 percent of the maximum width of the cavity for the fixing means. (Percent, Minimum) | % (upto1 digit) | NA | 12.4 | IS 14772 | 2 | [15 empty] | 10
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.5 | CONSTRUCTION : Boxes and Enclosures with Inlets for Flexible Cables | Yes | Mandatory | Inlets (outlets) provided in boxes and enclosures classified according to 7.3.2 shall be so designed and constructed that the flexible cables can be easily introduced, and will not damage the flexible cable where it enters the box or enclosure impairing its further use. | Satisfactory/Unsatisfactory | NA | 12.5 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.6 | CONSTRUCTION : Boxes and Enclosures with Inlets for Applications other than Flexible Cables | Yes | Mandatory | An inlet opening for conduit entries, or at least two of them if there is more than one, shall be capable of accepting either conduits of sizes, or a combination of sizes, in accordance with the requirements of IS 14763 and/or IEC 60981. Compliance is checked by inspection with the appropriate cables or conduits installed. Inlet openings of adequate size may also be obtained by the use of knock-outs or suitable insertion pieces or by means of an appropriate cutting tool. | Satisfactory/Unsatisfactory | NA | 12.6 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.7 | CONSTRUCTION : Boxes and Enclosures with a Cable Anchorage(s) | Yes | Mandatory | The cable is then subjected 50 times for 1 s to a pull force as specified in Table 3 and immediately afterwards the flexible cable is subjected to a torque not less than the relevant value specified in Table 3 for (15 ± 1) s applied as near as practicable to the cable entry. After the tests, the flexible cable shall not have been displaced by more than 2 mm and the cable anchorage (strain relief) shall not show any damage which leads to non-compliance with this standard. (mm, Maximum) | mm (upto 2 decimal digit) | NA | 12.7 | IS 14772 | [19 empty] | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.8 | CONSTRUCTION : Boxes and Enclosures with Cable Retention Means | Yes | Mandatory | The load is maintained for 1 min and at the end of this period, the displacement of the cable shall not exceed 3 mm following the removal of the load. (mm, Maximum) | mm (upto 2 decimal digit) | cable of the maximum nominal cross -sectional area and a cable with the minimum nominal cross-sectional area, manufacturer‘s instructions | 12.8 | IS 14772 | [21 empty] | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.9.1 | CONSTRUCTION : Knock-outs Intended to be Removed by Mechanical Impact : General | Yes | Mandatory | It shall be possible to remove knock-outs intended to be removed by mechanical impact without damaging the box. | Satisfactory/Unsatisfactory | NA | 12.9.1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.9.1 | CONSTRUCTION : Knock-outs Intended to be Removed by Mechanical Impact : General | Yes | Mandatory | Knock-outs intended for use with cables shall be free from chips or burrs. | Satisfactory/Unsatisfactory | NA | 12.9.2 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.9.1 | CONSTRUCTION : Knock-outs Intended to be Removed by Mechanical Impact : General | Yes | Mandatory | In knock- outs intended for use with conduits and/ or a grommet or a membrane, chips and burrs are disregarded. | Satisfactory/Unsatisfactory | NA | 12.9.3 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.9.1 | CONSTRUCTION : Knock-outs Intended to be Removed by Mechanical Impact : General | Yes | Mandatory | In order to close an open knock-out in a box or an enclosure classified according to 7.1.2 a blanking-plug can be used. | Satisfactory/Unsatisfactory | NA | 12.9.4 | IS 14772 | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.9.2 | CONSTRUCTION : Knock-outs Intended to be Removed by Mechanical Impact : Knock-out Retention | Yes | Mandatory | The knock-out shall remain in place and the degree of protection of the box or enclosure shall be unchanged when measured 1 h after the force has been removed. | Satisfactory/Unsatisfactory | NA | 12.10 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.9.3 | CONSTRUCTION : Knock-outs Intended to be Removed by Mechanical Impact : Knock-out Removal | Yes | Mandatory | After the test, there shall be no sharp edges, except for knock-outs for conduits and/or for use with a grommet or a membrane and the box and enclosure shall not be damaged. | Satisfactory/Unsatisfactory | NA | 12.11 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.9.4 | CONSTRUCTION : Knock-outs Intended to be Removed by Mechanical Impact : Flat Surfaces Surrounding Knock-outs | Yes | Mandatory | Compliance is checked by inspection and by measurement according to the appropriate national standard sheet, if any. | Satisfactory/Unsatisfactory | NA | 12.11 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.10 | CONSTRUCTION : Screw Fixings | Yes | Mandatory | During the test, there shall be no damage, such as breakage of screw or damage to the head slot (rendering the use of the appropriate screwdriver impossible) or to the threads or to the enclosure impairing the further use of the fixing means. The screws shall be gradually tightened in one smooth and continuous movement. | Satisfactory/Unsatisfactory | NA | 12.11 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.11 | CONSTRUCTION : Fixing of Boxes and Enclosures Classified According to 7.2.1 | Yes | Mandatory | Flush type boxes and enclosures other than for hollow walls, and as otherwise indicated below, shall be provided with fixing means for their suitable attachment to the wall, ceiling or floor. Screws intended to fix the box or enclosure to the building structure need not be supplied with the box or enclosure but can be provided by the installer according to the manufacturer’s instructions. | Satisfactory/Unsatisfactory | NA | 12.12, a) | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.11 | CONSTRUCTION : Fixing of Boxes and Enclosures Classified According to 7.2.1 | Yes | Mandatory | Separately supplied fixing means for a box or enclosure shall comply with the requirements for the fixing means of the box or enclosure with which they are intended to be used and shall include a means for fixing to the box or enclosure. | Satisfactory/Unsatisfactory | NA | 12.12, a) | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.11 | CONSTRUCTION : Fixing of Boxes and Enclosures Classified According to 7.2.1 | Yes | Mandatory | After the test the specimen shall not have been displaced by more than 0.5 mm from the mounting block. (mm, Maximum) | mm (upto 2 decimal digit) | NA | 12.12, b) | IS 14772 | 3 | [22 empty] | 0.5
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.12, a) | CONSTRUCTION : Fixing of Flush Type and Semi-flush Type Boxes and Enclosures Classified According to 7.2.2.1 | Yes | Mandatory | After this test, the specimens shall show no damage impairing their further use and | Satisfactory/Unsatisfactory | NA | 12.13.1 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.12, a) | CONSTRUCTION : Fixing of Flush Type and Semi-flush Type Boxes and Enclosures Classified According to 7.2.2.1: Checking pull and torque | Yes | Mandatory | After this test, the displacement of the lever shall be no more than 2°. (degree, Maximum) | Angle in ° (upto 2 decimal digit) | NA | 12.13.2 | IS 14772 | 2 | [24 empty] | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.12, b) | CONSTRUCTION : Fixing of Flush Type and Semi-flush Type Boxes and Enclosures Classified According to 7.2.2.1: Checking displacement | Yes | Mandatory | After the test, the edge of the box shall not have been displaced by more than 1 mm in comparison to the mounting surface. (mm, Maximum) | mm (upto 2 decimal digit) | NA | 12.13.2 | IS 14772 | [27 empty] | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.13.1 | CONSTRUCTION : Boxes and Enclosures Classified According to 7.2.2.2 and 7.2.2.3 : General | Yes | Mandatory | Boxes and enclosures for hollow walls or the like classified according to 7.2.2.2 and 7.2.2.3 shall have suitable means for fixing the box or the enclosure to hollow walls and hollow ceilings. | Satisfactory/Unsatisfactory | NA | 12.13.3 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.13.2 | CONSTRUCTION : Boxes and Enclosures Classified According to 7.2.2.2 and 7.2.2.3 : Boxes Intended for Mounting on a Wood Structural Member of a Wall | Yes | Mandatory | The assembly shall withstand a force of 225 N gradually applied centrally from the base of the box for a period of 5 min. | Satisfactory/Unsatisfactory | NA | 12.3.4 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.13.2 | CONSTRUCTION : Boxes and Enclosures Classified According to 7.2.2.2 and 7.2.2.3 : Boxes Intended for Mounting on a Wood Structural Member of a Wall | Yes | Mandatory | The assembly shall withstand a force of 225 N gradually applied centrally from the base of the box for a period of 5 min. After the removal of the force, there shall be no pulling out of the nails or screws used to mount the box or movement of the face of the box in the horizontal plane of more than 3 mm. (mm, Maximum) | mm (upto 2 decimal digit) | NA | 12.13.5 | IS 14772 | 2 | [28 empty] | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.13.3 | CONSTRUCTION : Boxes and Enclosures Classified According to 7.2.2.2 and 7.2.2.3 : Boxes Intended for Mounting to a Wooden Structural Member of a Ceiling | Yes | Mandatory | With the force still applied, the deflection of the face of the box shall not exceed 6 mm measured from a plane parallel to the horizontal face of the structural member. (mm, Maximum) | mm (upto 2 decimal digit) | NA | 12.13.6 | IS 14772 | [31 empty] | 6
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.3.4 | CONSTRUCTION : Boxes and Enclosures Classified According to 7.2.2.2 and 7.2.2.3 : Boxes Intended for Mounting to a Steel-stud Structural Member of a Wall | Yes | Mandatory | The assembly shall withstand a force of 180 N gradually applied centrally from the face of the box for a period of 5 min. With the force still applied, the deflection of the box shall not exceed 2 mm in either direction. (mm, Maximum) | mm (upto 2 decimal digit) | NA | 12.14 | IS 14772 | [33 empty] | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 12.13.5 | CONSTRUCTION : Boxes and Enclosures Classified According to 7.2.2.2 and 7.2.2.3 : Internal Volume of Boxes and Enclosures Classified According to 7.2.2.2 and 7.2.2.3 | Yes | Mandatory | A box or enclosure provided with a partition shall have the volume of each partitioned section verified. Compliance is checked by the test of 12.16. | Satisfactory/Unsatisfactory | internal volume of a box | IS 14772 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.13.6 | CONSTRUCTION : Boxes and Enclosures Classified According to 7.2.2.2 and 7.2.2.3 :Boxes Intended for Mounting in a Finished Structure | Yes | Mandatory | A screw that strips before being tightened to the torque specified shall not over ride more than once. The screw shall be capable of being removed by a screw driver. | Satisfactory/Unsatisfactory | NA | IS 14772 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.14 | CONSTRUCTION : Cable Gland Entry | Yes | Mandatory | After the test, the boxes and enclosures shall show no damage within the meaning of this standard. | Satisfactory/Unsatisfactory | NA | IS 14772 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.15.2 | CONSTRUCTION : Boxes and Enclosures with Inlets (Outlets) or Spouts (hubs) for Conduits | Yes | Mandatory | The inlet spout shall prevent further entry of the conduit into the box. | Satisfactory/Unsatisfactory | NA | IS 14763 or IEC 60981 | IS 14763 or IEC 60981
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.15.3 | CONSTRUCTION : Boxes and Enclosures with Inlets (Outlets) or Spouts (hubs) for Conduits | Yes | Mandatory | The conduit shall not come loose from the inlet spout of the enclosure. | Satisfactory/Unsatisfactory | NA | IS 14763 or IEC 60981 | IS 14763 or IEC 60981
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.15.4 | CONSTRUCTION : Boxes and Enclosures with Inlets (Outlets) or Spouts (hubs) for Conduits | Yes | Mandatory | The inlet spout shall not come loose or be damaged and the conduit shall stay within the inlet spout. | Satisfactory/Unsatisfactory | NA | IS 14772 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 12.16 | CONSTRUCTION : Internal Volume of Boxes and Enclosures | Yes | Mandatory | The volume of a side pocket provided to increase the volume of a box or enclosure shall be calculated using a depth-of-pocket not more than the smallest dimension of the opening into that side pocket. | Satisfactory/Unsatisfactory | NA | IS 14772 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 13.1.1 | Resistance to Ageing | Yes | Mandatory | After the test, the specimen shall show no harmful deformation or similar damage, which may impair their further use within the meaning of this standard. | Satisfactory/Unsatisfactory | NA | IS 14772 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 13.1.2 | Resistance to Ageing | Yes | Mandatory | During these tests, the grommets, blanking plugs and/or membranes shall not be deformed to such an extent that live parts of any included accessory become accessible. | Satisfactory/Unsatisfactory | NA | IS 14772 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 13.1.2 | Resistance to Ageing | Yes | Mandatory | After the test, grommets, blanking plugs and/or membranes shall show no harmful deformation, cracks or similar damage which would lead to non-compliance with this standard. | Satisfactory/Unsatisfactory | NA | IS 14772 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 13.1.3 | Resistance to Ageing | Yes | Mandatory | After the test, the grommets, blanking plugs or entry membranes shall show no harmful deformation, cracks or similar damage which would lead to non-compliance with this standard. | Satisfactory/Unsatisfactory | NA | IS 14772 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 13.2 | Protection Against the Ingress of Solid Objects | Yes | Mandatory | For degree of protection IP5X, the test is carried out according to IS/IEC 60529 category 2 and the drain holes, if any, shall not be open. For degrees of protection up to and including IP4X, the protection is satisfactory if the full diameter of the probe does not pass through any opening other than through drain holes, in which case the probe shall not touch live parts within the enclosure. For degree of protection IP5X, the protection is satisfactory if the dust does not cover the whole inner surface. For degree of protection IP6X, the test is carried out according to IS/IEC 60529 and the drain hole, if any, shall not be open. The protection is satisfactory if there is no dust inside the box or enclosure. | Satisfactory/Unsatisfactory | IP5X, IP4X, IP6X | IS/IEC 60529 | IS/IEC 60529
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 13.3.2 | Protection Against Harmful Ingress of Water | Yes | Mandatory | During the tests of enclosures of degree of protection higher than IPX4, drain holes, if any, shall not be opened. | Satisfactory/Unsatisfactory | IPX4, IPX5 | IS/IEC 60529 | IS/IEC 60529
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 13.3.3 | Protection Against Harmful Ingress of Water | Yes | Mandatory | After the test, the specimens of boxes and enclosures classified according to 7.1.1, 7.1.3 and 7.1.4, as appropriate, shall withstand an electric strength test specified in 14.3, which shall be started within 5 min of the completion of the test according to this sub clause. | Withstood the test/Failed in the test | NA | 13.3.3 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 13.3.4 | Protection Against Harmful Ingress of Water | Yes | Mandatory | Immediately after the test, the indicator paper shall still be dry. | Satisfactory/Unsatisfactory | NA | 13.3.4 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 14.1 | INSULATION RESISTANCE AND ELECTRIC STRENGTH | Yes | Mandatory | After this treatment, the specimen shall show no damage impairing its further use and shall pass the following tests. | Satisfactory/Unsatisfactory | NA
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 14.2 | INSULATION RESISTANCE AND ELECTRIC STRENGTH | Yes | Mandatory | The insulation resistance shall be not less than 5 MΩ. (MΩ, Minimum) | Mega Ohms (upto 1 digit) | NA | 14.2 | IS 14772 | [34 empty] | 5
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 14.3 | INSULATION RESISTANCE AND ELECTRIC STRENGTH | Yes | Mandatory | The electric strength is tested by applying a voltage of a substantially sinusoidal waveform, having a nominal frequency of 50 Hz or 60 Hz and a value as specified in Table 6, for 1 min between the parts listed in 14.2. No flashover or breakdown shall occur during the test | Withstood the test/Failed in the test | NA | 14.3 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 15.2 | Mechanical Strength : Impact Test at Low Temperature | Yes | Mandatory | After the test, the specimens shall show no damage leading to non-compliance with the standard | Satisfactory/Unsatisfactory | NA | 15.2 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 15.2 | Mechanical Strength : Impact Test at Low Temperature | Yes | Mandatory | Damage to the finish, small dents and small chips which do not adversely affect the protection against electric shock or harmful ingress of water are disregarded. | Satisfactory/Unsatisfactory | NA | 15.2 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 15.2 | Mechanical Strength : Impact Test at Low Temperature | Yes | Mandatory | Cracks passing through the material not visible with normal or corrected vision without magnification, surface cracks in fibre-reinforced mouldings and small indentations are disregarded. | Satisfactory/Unsatisfactory | NA | 15.2 | IS 14772 | 3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 15.3 | Mechanical Strength - Compression Test | Yes | Mandatory | After the test, the boxes and enclosures shall show neither deformation nor damage leading to non compliance with the standard. | Satisfactory/Unsatisfactory | NA | 15.3 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 15.3 | Mechanical Strength - Compression Test | Yes | Mandatory | After the test, the box and the enclosure shall show no deformation or damage leading to non-compliance with the standard or affecting its further intended use. | Satisfactory/Unsatisfactory | NA | 15.3 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 15.4 | Mechanical Strength - Impact Test for Boxes and Enclosures | Yes | Mandatory | After the test, the specimens shall show no damage leading to non-compliance with the standard. | Cracks Not Observed/Cracks Observed | NA | 15.4 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 15.4 | Mechanical Strength - Impact Test for Boxes and Enclosures | Yes | Mandatory | There shall be no cracks passing through the material which are visible to normal or corrected vision without magnification. Surface cracks in fibre-reinforced mouldings and small indentations are ignored. | Satisfactory/Unsatisfactory | NA | 15.4 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 15.5 | Mechanical Strength - Compression Test for Enclosures Made of Natural or Synthetic Rubber or a Mixture of Both | Yes | Mandatory | The permanent deformation at any point on the cover, excluding the deflection of the plywood and gasket compression, shall not exceed 1 mm, measured 1 h after the load is removed. | Less than 1 mm/More than 1 mm | NA | 15.5 | IS 14772 | 1 | [36 empty] | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 15.5 | Mechanical Strength - Compression Test for Enclosures Made of Natural or Synthetic Rubber or a Mixture of Both | Yes | Mandatory | After the test, the boxes or enclosures shall show no damage leading to non-compliance with this standard. | Satisfactory/Unsatisfactory | NA | 15.5 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 16.1 | Resistance to Heat : Parts of Insulating Material Necessary to Retain Current-carrying Parts | Yes | Mandatory | The diameter of the impression caused by the ball is measured and shall not exceed 2 mm. (mm, Maximum) | mm (upto 2 decimal digit) | Parts of Insulating Material Necessary to Retain Current-carrying Parts | 16.1 | IS 14772 | [39 empty] | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 16.3.1 | Resistance to Heat : Boxes and Enclosures of Insulating Materials Classified According to 7.2.2.2 or 7.2.2.3 : Mechanical Strength | Yes | Mandatory | The screws securing the crossbar to the box shall not have pulled out more than 6.3 mm. (mm, Maximum) | mm (upto 2 decimal digit) | NA | 16.3.1 | IS 14772 | 1 | [40 empty] | 6.3
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 16.3.1 | Resistance to Heat : Boxes and Enclosures of Insulating Materials Classified According to 7.2.2.2 or 7.2.2.3 : Mechanical Strength | Yes | Mandatory | The screws shall be able to be removed by a screwdriver using a torque not exceeding 2.3 Nm. | Satisfactory/Unsatisfactory | NA | 16.3.1 | IS 14772 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 16.3.2 | Resistance to Heat : Boxes and Enclosures of Insulating Materials Classified According to 7.2.2.2 or 7.2.2.3 : Parts of Insulating Material Necessary to Retain Parts of the Earthing Circuit | Yes | Mandatory | Parts of insulating material necessary to retain the earthing strap described in 11.2 shall be subjected to a pull test before and after ageing. After each test, the earthing strap shall not become loose or detached from the specimen. | Satisfactory/Unsatisfactory | NA | 16.3.2 | IS 14772
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 17 | CREEPAGE DISTANCES, CLEARANCES AND DISTANCES THROUGH SEALING COMPOUND | Yes | Mandatory | a) Creepage distances and clearances: 1) between live parts of different polarity; and (mm, Minimum) | mm (upto 2 decimal digit) | Rated Voltage | 17 | IS 14772 | 1 | [41 empty] | 3 |  | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 17 | CREEPAGE DISTANCES, CLEARANCES AND DISTANCES THROUGH SEALING COMPOUND | Yes | Mandatory | a) Creepage distances and clearances: 2) between live parts .(mm, Minimum) | mm (upto 2 decimal digit) | NA | 17 | IS 14772 | 2 | [41 empty] | 3 |  | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 17 | CREEPAGE DISTANCES, CLEARANCES AND DISTANCES THROUGH SEALING COMPOUND | Yes | Mandatory | b) metal covers and boxes without insulating lining; or (mm, Minimum) | mm (upto 2 decimal digit) | Rated Voltage | 17 | IS 14772 | 3 | [41 empty] | 3 |  | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 17 | CREEPAGE DISTANCES, CLEARANCES AND DISTANCES THROUGH SEALING COMPOUND | Yes | Mandatory | c) the surface on which the box is mounted. (mm, Minimum) | mm (upto 2 decimal digit) | NA | 17 | IS 14772 | 4 | [41 empty] | 3 |  | 4
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 18 | Resistance to insulating Material to Abnormal Heat and Fire | Yes | Mandatory | The specimen is regarded as having passed the glow wire test if: a) there is no visible flame and no sustained glowing, or if b) flames and glowing at the specimen extinguish within 30 s after the removal of the glow wire. | Satisfactory/Unsatisfactory | NA | clauses 4 to 10 of IEC 60695 2-11 | clauses 4 to 10 of IEC 60695 2-11 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 18 | Resistance to insulating Material to Abnormal Heat and Fire | Yes | Mandatory | There shall be no ignition of the tissue paper or scorching of the board. | Satisfactory/Unsatisfactory | NA | clauses 4 to 10 of IEC 60695 2-11 | clauses 4 to 10 of IEC 60695 2-11 | 2
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 19 | Resistance toTracking | Yes | Mandatory | No flashover or breakdown between electrodes shall occur before a total of 50 drops has fallen. | Satisfactory/Unsatisfactory | NA | 19 | IS 14772 | 1
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Quantitative | 19 | Resistance toTracking | Yes | Mandatory | Alternatively, the CTI value for the material may be used. The CTI value shall not be less than 175, ( CTI value, Minimum) | CTI value (upto1 digit) | NA | 19 | IS 14772 | 2 |  |  | CTI value | [42 empty] | 175
IS 14772 | NA | NA | 2020 | 0 | BOXES AND ENCLOSURES FOR ELECTRICAL ACCESSORIES FOR HOUSEHOLD AND SIMILAR FIXED ELECTRICAL INSTALLATIONS | Electrical | Qualitative | 20 | Resistance to Corrossion | Yes | Mandatory | their surface shall show no sign of rust. Traces of rust on cut edges and any yellowish film removable by rubbing are ignored. Cut edges also include punched holes and thread surfaces of tapped holes. | Satisfactory/Unsatisfactory(Rust observed) | NA | 20 | IS 14772

## Test request formatIS 14772 202
Rated voltage | Standard rated connecting capacities | The Nature of their Material | The Type of Installation | [6 empty] | Ceilings, Floors or Furniture | [6 empty] | The Clamping Means |  |  |  | The Minimum Temperature during installation |  |  | The degree of protection against access to hazardous parts and against harmful effects due to the ingress of solid foreign objects according to IS/IEC 60529 with a minimum degree of IP2X | The degree of protection against harmful effects due to the ingress of water according to IS/IEC 60529 | The degree of protection of the part mounted inside the hollow walls of the boxes classified according to 7.2.2.1 |  | The provision for fixing accessories to boxes |  |  |  | The method of fixing the terminals or connecting devices in the connecting box |  |  |  | 9.1 Boxes and enclosures shall comply with the appropriate standard sheets, if any. | Internal volume of a box
250 V/ 400 V a.c. | 0.5 mm²/ 0.75 mm², 1 mm²/ 1.5 mm²/2.5 mm²/ 4 mm²/ 6 mm²/ 10 mm²/ 16 mm²/ 25 mm²/ 35 mm². | Insulating/ Metallic/ Composite/ Natural or Synthetic Rubber or a Mixture of both | Flush, Semi-flush in Solid Walls, Ceilings or Floors |  |  | Flush or Semi-flush in Hollow Walls, Hollow Ceilings, Hollow Floors or Furniture |  |  | Surface Mounting on Walls, Ceilings, Floors or Furniture | With Inlets for Sheathed Cables for Fixed Installations | With Inlets for Flexible Cables | With Inlets for Plain Or corrugated Conduits | With Inlets for Threaded Conduits | With Inlets for Other Types of Conductors/Cables or Conduits | With Spouts ( hub) | Without Inlets — Inlet openings will be made during installation | With Cable Retention | With Cable Anchorage | With Clamping Means for Flexible Conduit | Without Clamping Means | –5 °C | –15 °C | –25 °C |  |  | IP2X | > IP2X | Boxes Supplied with Screws | Boxes Intended to Receive Screws | Boxes Intended to Receive Claws | Boxes Intended to Receive Other Means | With integrated clamping units | With incorporated terminals or connecting devices | With provisions for subsequent incorporation of terminals or connecting devices | Without fixing (for floating terminals or connecting devices)
|  |  | Not suitable for installation into concrete | Suitable for installation into concrete with a maximum temperature during the casting Process of +60 °C | Suitable for installation into concrete with a maximum temperature during the casting process of +90 °C | Class Ha | Class Hb for walls | Class Hb for ceilings