## 1554-1
IS No. | Part | Section | Year | No. of Amendments | Title of the Standard | Type of Test | Qualitative or Quantitative | Clause/ Table/ Annex Reference | Test Parameter Name | To be tested and/or reported by Lab (Yes/No) | Mandatory or Optional | Requirement (as per Indian Standard) | Test Result/ Observation | Test Request Requirements | Test Method Reference | Test Method Reference Standard | Sl No. under Clause/ Table/ Annex Reference | Sample Quantity | Equipment |  |  |  | Nominal area of conductor 1.5 sqmm, single core armoured | Nominal area of conductor 1.5 sqmm, single core unarmoured / multicore | Nominal area of conductor 2.5 sqmm, single core armoured | Nominal area of conductor 2.5 sqmm, single core unarmoured / multicore | Nominal area of conductor 4 sqmm, single core armoured | Nominal area of conductor 4 sqmm, single core unarmoured / multicore | Nominal area of conductor 6 sqmm, single core armoured | Nominal area of conductor 6 sqmm, single core unarmoured / multicore | Nominal area of conductor 10 sqmm, single core armoured | Nominal area of conductor 10 sqmm, single core unarmoured / multicore | Nominal area of conductor 16 sqmm, single core armoured | Nominal area of conductor 16 sqmm, single core unarmoured / multicore | Nominal area of conductor 25 sqmm, single core armoured | Nominal area of conductor 25 sqmm, single core unarmoured / multicore | Nominal area of conductor 35 sqmm, single core armoured | Nominal area of conductor 35 sqmm, single core unarmoured / multicore | Nominal area of conductor 50 sqmm, single core armoured | Nominal area of conductor 50 sqmm, single core unarmoured / multicore | Nominal area of conductor 70 sqmm, single core armoured | Nominal area of conductor 70 sqmm, single core unarmoured / multicore | Nominal area of conductor 95 sqmm, single core armoured | Nominal area of conductor 95 sqmm, single core unarmoured / multicore | Nominal area of conductor 120 sqmm, single core armoured | Calculated diameter over laid up cores Up to 25 mm | Calculated diameter over laid up cores Over 25 up to 35 mm | Calculated diameter over laid up cores Over 35 up to 45 mm | Calculated diameter over laid up cores Over 45 up to 55 mm | Calculated diameter over laid up cores Over 55 mm | 1.5 mm² – Two core (round wire) | 1.5 mm² – Three core (round wire) | 1.5 mm² – Four core (round wire) | 2.5 mm² – Two core (round wire) | 2.5 mm² – Three core (round wire) | 2.5 mm² – Four core (round wire) | 4 mm² – Two core (round wire) | 4 mm² – Three core (round wire) | 4 mm² – Four core (round wire) | 6 mm² – Two core (round wire) | 6 mm² – Three core (round wire) | 6 mm² – Four core (round wire) | 10 mm² – Two core (round wire) | 10 mm² – Three core (round wire) | 10 mm² – Four core (round wire) | 16 mm² – Two core (round wire) | 16 mm² – Three core (round wire) | 16 mm² – Four core (round wire) | 25 mm² – Two core (round wire) | 25 mm² – Three core (round wire) | 25 mm² – Four core (round wire) | 25 mm² – Four core (reduced neutral, round wire) | 35 mm² – Two core (round wire) | 35 mm² – Three core (round wire) | 35 mm² – Four core (round wire) | 35 mm² – Four core (reduced neutral, round wire) | 50 mm² – Two core (round wire) | 50 mm² – Three core (round wire) | 50 mm² – Four core (round wire) | 50 mm² – Four core (reduced neutral, round wire) | 70 mm² – Two core (round wire) | 70 mm² – Three core (round wire) | 70 mm² – Four core (round wire) | 70 mm² – Four core (reduced neutral, round wire) | 95 mm² – Two core (round wire) | 95 mm² – Three core (round wire) | 95 mm² – Four core (round wire) | 95 mm² – Four core (reduced neutral, round wire) | 120 mm² – Two core (round wire) | 120 mm² – Three core (round wire) | 120 mm² – Four core (round wire) | 120 mm² – Four core (reduced neutral, round wire) | 150 mm² – Two core (round wire) | 150 mm² – Three core (round wire) | 150 mm² – Four core (round wire) | 150 mm² – Four core (reduced neutral, round wire) | 185 mm² – Two core (round wire) | 185 mm² – Three core (round wire) | 185 mm² – Four core (round wire) | 185 mm² – Four core (reduced neutral, round wire) | 240 mm² – Two core (round wire) | 240 mm² – Three core (round wire) | 240 mm² – Four core (round wire) | 240 mm² – Four core (reduced neutral, round wire) | 300 mm² – Two core (round wire) | 300 mm² – Three core (round wire) | 300 mm² – Four core (round wire) | 300 mm² – Four core (reduced neutral, round wire) | 400 mm² – Two core (round wire) | 400 mm² – Three core (round wire) | 400 mm² – Four core (round wire) | 400 mm² – Four core (reduced neutral, round wire) | 500 mm² – Two core (round wire) | 500 mm² – Three core (round wire) | 500 mm² – Four core (round wire) | 500 mm² – Four core (reduced neutral, round wire) | 630 mm² – Two core (round wire) | 630 mm² – Three core (round wire) | 630 mm² – Four core (round wire) | 630 mm² – Four core (reduced neutral, round wire) | Up to 15 mm – Unarmoured (Nominal) | Up to 15 mm – Unarmoured (Minimum) | Up to 15 mm – Armoured (Minimum) | Over 15 up to 25 mm – Unarmoured (Nominal) | Over 15 up to 25 mm – Unarmoured (Minimum) | Over 15 up to 25 mm – Armoured (Minimum) | Over 25 up to 35 mm – Unarmoured (Nominal) | Over 25 up to 35 mm – Unarmoured (Minimum) | Over 25 up to 35 mm – Armoured (Minimum) | Over 35 up to 40 mm – Unarmoured (Nominal) | Over 35 up to 40 mm – Unarmoured (Minimum) | Over 35 up to 40 mm – Armoured (Minimum) | Over 40 up to 45 mm – Unarmoured (Nominal) | Over 40 up to 45 mm – Unarmoured (Minimum) | Over 40 up to 45 mm – Armoured (Minimum) | Over 45 up to 50 mm – Unarmoured (Nominal) | Over 45 up to 50 mm – Unarmoured (Minimum) | Over 45 up to 50 mm – Armoured (Minimum) | Over 50 up to 55 mm – Unarmoured (Nominal) | Over 50 up to 55 mm – Unarmoured (Minimum) | Over 50 up to 55 mm – Armoured (Minimum) | Over 55 up to 60 mm – Unarmoured (Nominal) | Over 55 up to 60 mm – Unarmoured (Minimum) | Over 55 up to 60 mm – Armoured (Minimum) | Over 60 up to 65 mm – Unarmoured (Nominal) | Over 60 up to 65 mm – Unarmoured (Minimum) | Over 60 up to 65 mm – Armoured (Minimum) | Over 65 up to 70 mm – Unarmoured (Nominal) | Over 65 up to 70 mm – Unarmoured (Minimum) | Over 65 up to 70 mm – Armoured (Minimum) | Over 70 up to 75 mm – Unarmoured (Nominal) | Over 70 up to 75 mm – Unarmoured (Minimum) | Over 70 up to 75 mm – Armoured (Minimum) | Over 75 mm – Unarmoured (Nominal) | Over 75 mm – Unarmoured (Minimum) | Over 75 mm – Armoured (Minimum) | 0.5 mm² – Copper (plain) | 0.5 mm² – Copper (tinned) | 0.75 mm² – Copper (plain) | 0.75 mm² – Copper (tinned) | 1 mm² – Copper (plain) | 1 mm² – Copper (tinned) | 1.5 mm² – Copper (plain) | 1.5 mm² – Copper (tinned) | 1.5 mm² – Aluminium Circular or shaped | 2.5 mm² – Copper (plain) | 2.5 mm² – Copper (tinned) | 2.5 mm² – Aluminium | 4 mm² – Copper (plain) | 4 mm² – Copper (tinned) | 4 mm² – Aluminium | 6 mm² – Copper (plain) | 6 mm² – Copper (tinned) | 6 mm² – Aluminium | 10 mm² – Copper (plain) | 10 mm² – Copper (tinned) | 10 mm² – Aluminium | 16 mm² – Copper (plain) | 16 mm² – Copper (tinned) | 16 mm² – Aluminium | 25 mm² – Copper (plain) | 25 mm² – Aluminium | 35 mm² – Copper (plain) | 35 mm² – Aluminium | 50 mm² – Copper (plain) | 50 mm² – Aluminium | 70 mm² – Copper (plain) | 70 mm² – Aluminium | 95 mm² – Copper (plain) | 95 mm² – Aluminium | 120 mm² – Copper (plain) | 120 mm² – Aluminium | 150 mm² – Copper (plain) | 150 mm² – Aluminium | 185 mm² – Aluminium | 240 mm² – Aluminium | 300 mm² – Aluminium | 1 mm² – Copper (plain) | 1 mm² – Copper (tinned) | 1 mm² – Aluminium | 1.5 mm² – Copper (plain) | 1.5 mm² – Copper (tinned) | 1.5 mm² – Aluminium | 2.5 mm² – Copper (plain) | 2.5 mm² – Copper (tinned) | 2.5 mm² – Aluminium | 4 mm² – Copper (plain) | 4 mm² – Copper (tinned) | 4 mm² – Aluminium | 6 mm² – Copper (plain) | 6 mm² – Copper (tinned) | 6 mm² – Aluminium | 10 mm² – Copper (plain) | 10 mm² – Copper (tinned) | 10 mm² – Aluminium | 16 mm² – Copper (plain) | 16 mm² – Copper (tinned) | 16 mm² – Aluminium | 25 mm² – Copper (plain) | 25 mm² – Copper (tinned) | 25 mm² – Aluminium | 35 mm² – Copper (plain) | 35 mm² – Copper (tinned) | 35 mm² – Aluminium | 50 mm² – Copper (plain) | 50 mm² – Copper (tinned) | 50 mm² – Aluminium | 70 mm² – Copper (plain) | 70 mm² – Copper (tinned) | 70 mm² – Aluminium | 95 mm² – Copper (plain) | 95 mm² – Copper (tinned) | 95 mm² – Aluminium | 120 mm² – Copper (plain) | 120 mm² – Copper (tinned) | 120 mm² – Aluminium | 150 mm² – Copper (plain) | 150 mm² – Copper (tinned) | 150 mm² – Aluminium | 185 mm² – Copper (plain) | 185 mm² – Copper (tinned) | 185 mm² – Aluminium | 240 mm² – Copper (plain) | 240 mm² – Copper (tinned) | 240 mm² – Aluminium | 300 mm² – Copper (plain) | 300 mm² – Copper (tinned) | 300 mm² – Aluminium | 400 mm² – Copper (plain) | 400 mm² – Copper (tinned) | 400 mm² – Aluminium | 500 mm² – Copper (plain) | 500 mm² – Copper (tinned) | 500 mm² – Aluminium | 630 mm² – Copper (plain) | 630 mm² – Copper (tinned) | 630 mm² – Aluminium | 800 mm² – Copper (plain) | 800 mm² – Copper (tinned) | 800 mm² – Aluminium | 1000 mm² – Copper (plain) | 1000 mm² – Copper (tinned) | 1000 mm² – Aluminium | 1200 mm² – Copper (plain) | 1200 mm² – Copper (tinned) | 1200 mm² – Aluminium | 1400 mm² – Copper (plain) | 1400 mm² – Copper (tinned) | 1400 mm² – Aluminium | 1600 mm² – Copper (plain) | 1600 mm² – Copper (tinned) | 1600 mm² – Aluminium | 1800 mm² – Copper (plain) | 1800 mm² – Copper (tinned) | 1800 mm² – Aluminium | 2000 mm² – Copper (plain) | 2000 mm² – Copper (tinned) | 2000 mm² – Aluminium | 2500 mm² – Copper (plain) | 2500 mm² – Copper (tinned) | 2500 mm² – Aluminium | 1 mm² – Cu (circular, non‑compacted) | 1.5 mm² – Cu (circular, non‑compacted) | 1.5 mm² – Al (circular, non‑compacted) | 2.5 mm² – Cu (circular, non‑compacted) | 2.5 mm² – Al (circular, non‑compacted) | 4 mm² – Cu (circular, non‑compacted) | 4 mm² – Al (circular, non‑compacted) | 6 mm² – Cu (circular, non‑compacted) | 6 mm² – Al (circular, non‑compacted) | 10 mm² – Cu (circular, non‑compacted) | 10 mm² – Al (circular, non‑compacted) | 10 mm² – Cu (compacted / shaped) | 16 mm² – Cu (circular, non‑compacted) | 16 mm² – Al (circular, non‑compacted) | 16 mm² – Cu (compacted / shaped) | 16 mm² – Al (compacted / shaped) | 25 mm² – Cu (circular, non‑compacted) | 25 mm² – Al (circular, non‑compacted) | 25 mm² – Cu (compacted / shaped) | 25 mm² – Al (compacted / shaped) | 35 mm² – Cu (circular, non‑compacted) | 35 mm² – Al (circular, non‑compacted) | 35 mm² – Cu (compacted / shaped) | 35 mm² – Al (compacted / shaped) | 50 mm² – Cu (circular, non‑compacted) | 50 mm² – Al (circular, non‑compacted) | 50 mm² – Cu (compacted / shaped) | 50 mm² – Al (compacted / shaped) | 70 mm² – Cu (circular, non‑compacted) | 70 mm² – Al (circular, non‑compacted) | 70 mm² – Cu (compacted / shaped) | 70 mm² – Al (compacted / shaped) | 95 mm² – Cu (circular, non‑compacted) | 95 mm² – Al (circular, non‑compacted) | 95 mm² – Cu (compacted / shaped) | 95 mm² – Al (compacted / shaped) | 120 mm² – Cu (circular, non‑compacted) | 120 mm² – Al (circular, non‑compacted) | 120 mm² – Cu (compacted / shaped) | 120 mm² – Al (compacted / shaped) | 150 mm² – Cu (circular, non‑compacted) | 150 mm² – Al (circular, non‑compacted) | 150 mm² – Cu (compacted / shaped) | 150 mm² – Al (compacted / shaped) | 185 mm² – Cu (circular, non‑compacted) | 185 mm² – Al (circular, non‑compacted) | 185 mm² – Cu (compacted / shaped) | 185 mm² – Al (compacted / shaped) | 240 mm² – Cu (circular, non‑compacted) | 240 mm² – Al (circular, non‑compacted) | 240 mm² – Cu (compacted / shaped) | 240 mm² – Al (compacted / shaped) | 300 mm² – Cu (circular, non‑compacted) | 300 mm² – Al (circular, non‑compacted) | 300 mm² – Cu (compacted / shaped) | 300 mm² – Al (compacted / shaped) | 400 mm² – Cu (circular, non‑compacted) | 400 mm² – Al (circular, non‑compacted) | 400 mm² – Cu (compacted / shaped) | 400 mm² – Al (compacted / shaped) | 500 mm² – Cu (circular, non‑compacted) | 500 mm² – Al (circular, non‑compacted) | 500 mm² – Cu (compacted / shaped) | 500 mm² – Al (compacted / shaped) | 630 mm² – Cu (circular, non‑compacted) | 630 mm² – Al (circular, non‑compacted) | 630 mm² – Cu (compacted / shaped) | 630 mm² – Al (compacted / shaped) | 800 mm² – Cu (circular, non‑compacted) | 800 mm² – Al (circular, non‑compacted) | 800 mm² – Cu (compacted / shaped) | 800 mm² – Al (compacted / shaped) | 1000 mm² – Cu (circular, non‑compacted) | 1000 mm² – Al (circular, non‑compacted) | 1000 mm² – Cu (compacted / shaped) | 1000 mm² – Al (compacted / shaped) | 0.5 mm² – Plain wire | 0.5 mm² – Tinned wire | 0.75 mm² – Plain wire | 0.75 mm² – Tinned wire | 1 mm² – Plain wire | 1 mm² – Tinned wire | 1.5 mm² – Plain wire | 1.5 mm² – Tinned wire | 2.5 mm² – Plain wire | 2.5 mm² – Tinned wire | 4 mm² – Plain wire | 4 mm² – Tinned wire | 6 mm² – Plain wire | 6 mm² – Tinned wire | 10 mm² – Plain wire | 10 mm² – Tinned wire | 16 mm² – Plain wire | 16 mm² – Tinned wire | 25 mm² – Plain wire | 25 mm² – Tinned wire | 35 mm² – Plain wire | 35 mm² – Tinned wire | 50 mm² – Plain wire | 50 mm² – Tinned wire | 70 mm² – Plain wire | 70 mm² – Tinned wire | 95 mm² – Plain wire | 95 mm² – Tinned wire | 120 mm² – Plain wire | 120 mm² – Tinned wire | 150 mm² – Plain wire | 150 mm² – Tinned wire | 185 mm² – Plain wire | 185 mm² – Tinned wire | 240 mm² – Plain wire | 240 mm² – Tinned wire | 300 mm² – Plain wire | 300 mm² – Tinned wire | 400 mm² – Plain wire | 400 mm² – Tinned wire | 500 mm² – Plain wire | 500 mm² – Tinned wire | 630 mm² – Plain wire | 630 mm² – Tinned wire | 0.5 mm² conductor | 0.75 mm² conductor | 1 mm² conductor | 1.5 mm² conductor | 2.5 mm² conductor | 4 mm² conductor | 6 mm² conductor | 10 mm² conductor | 16 mm² conductor | 25 mm² conductor | 35 mm² conductor | 50 mm² conductor | 70 mm² conductor | 95 mm² conductor | 120 mm² conductor | 150 mm² conductor | 185 mm² conductor | 240 mm² conductor | 300 mm² conductor | 400 mm² conductor | 500 mm² conductor | 630 mm² conductor | 0.5 mm² – Plain wire | 0.5 mm² – Tinned wire | 0.75 mm² – Plain wire | 0.75 mm² – Tinned wire | 1 mm² – Plain wire | 1 mm² – Tinned wire | 1.5 mm² – Plain wire | 1.5 mm² – Tinned wire | 2.5 mm² – Plain wire | 2.5 mm² – Tinned wire | 4 mm² – Plain wire | 4 mm² – Tinned wire | 6 mm² – Plain wire | 6 mm² – Tinned wire | 10 mm² – Plain wire | 10 mm² – Tinned wire | 16 mm² – Plain wire | 16 mm² – Tinned wire | 25 mm² – Plain wire | 25 mm² – Tinned wire | 35 mm² – Plain wire | 35 mm² – Tinned wire | 50 mm² – Plain wire | 50 mm² – Tinned wire | 70 mm² – Plain wire | 70 mm² – Tinned wire | 95 mm² – Plain wire | 95 mm² – Tinned wire | 120 mm² – Plain wire | 120 mm² – Tinned wire | 150 mm² – Plain wire | 150 mm² – Tinned wire | 185 mm² – Plain wire | 185 mm² – Tinned wire | 240 mm² – Plain wire | 240 mm² – Tinned wire | 300 mm² – Plain wire | 300 mm² – Tinned wire | 0.5 mm² conductor | 0.75 mm² conductor | 1 mm² conductor | 1.5 mm² conductor | 2.5 mm² conductor | 4 mm² conductor | 6 mm² conductor | 10 mm² conductor | 16 mm² conductor | 25 mm² conductor | 35 mm² conductor | 50 mm² conductor | 70 mm² conductor | 95 mm² conductor | 120 mm² conductor | 150 mm² conductor | 185 mm² conductor | 240 mm² conductor | 300 mm² conductor | 25 mm² conductor | 35 mm² conductor | 50 mm² conductor | 70 mm² conductor | 95 mm² conductor | 120 mm² conductor | 25 mm² conductor | 35 mm² conductor | 50 mm² conductor | 70 mm² conductor | 95 mm² conductor | 120 mm² conductor
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 3.1 | Material | Yes | Mandatory | The conductor shall be composed of plain copper or aluminium wires complying with IS : 8130-1984 | Copper/Aluminium | Material: Conductor | - | IS 8130-2013 | - | - | - | Referred IS 8130: 2013 has been put in the format | Cl. 9.2 | Nominal thickness of insulation (min) | 1.1 mm | 0.8 mm | 1.2 mm | 0.9 mm | 1.3 mm | 1.0 mm | 1.3 mm | 1.0 mm | 1.3 mm | 1.0 mm | 1.3 mm | 1.0 mm | 1.5 mm | 1.2 mm | 1.5 mm | 1.2 mm | 1.7 mm | 1.4 mm | 1.7 mm | 1.4 mm | 1.9 mm | 1.6 mm | 1.9 mm
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 3.1.1 | Material | Yes | Mandatory | Mining cable to be used in gassy mines shall be of copper conductor only | Copper conductor/ Not applicable (Not a mining cable) | Material: Conductor | - | - | - | - | - |  | Cl. 12.3 | Inner Sheath (min) | [23 empty] | 0.3 mm | 0.4 mm | 0.5 mm | 0.6 mm | 0.7 mm
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 4.1.1 | Insulation | Yes | Mandatory | General Purpose Insulaiion - The insulation shall be of Type A PVC compound conforming to the requirements of IS : 5831-1984 | Type A/ Not applicable (Not Type A) | Insulation : General Purpose Insulation, Type A | - | IS 5831-1984 | - | - | - |  | Cl. 13.5.1 | Maximum d.c. resistance of armour at 20 °C (Ω/km) | [28 empty] | 6.37 | 6.02 | 5.52 | 5.54 | 5.22 | 4.77 | 4.83 | 4.54 | 4.14 | 4.4 | 4.14 | 3.76 | 3.86 | 3.62 | 2.84 | 2.85 | 2.67 | 2.42 | 2.77 | 2.49 | 2.14 | 2.21 | 2.67 | 2.35 | 1.99 | 2.05 | 2.26 | 2.03 | 1.39 | 1.84 | 2.04 | 1.41 | 1.18 | 1.23 | 1.41 | 1.22 | 1.05 | 1.1 | 1.3 | 1.11 | 0.962 | 1.05 | 1.19 | 1 | 0.703 | 0.959 | 1.08 | 0.733 | 0.623 | 0.684 | 0.749 | 0.642 | 0.563 | 0.596 | 0.684 | 0.586 | 0.389 | 0.429 | 0.464 | 0.408 | 0.361 | 0.367 | 0.397 | 0.359 | 0.233 | 0.264 | 0.274 | 0.248 | 0.203 | 0.227
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 4.1.2 | Insulation | Yes | Mandatory | Heat Resisting Insulation - The insulation shall be of Type C PVC compound conforming to the requirements of IS : 5831-1984 | Type C/ Not applicable (Not Type C) | Insulation :Heat Resisting Insulation, Type C | - | IS 5831-1984 | - | - | - |  | Cl. 14.4.1 & Cl. 14.4.2 | Thickness of outer sheath in mm | [98 empty] | 1.8 | 1.24 | 1.24 | 2 | 1.4 | 1.4 | 2.2 | 1.56 | 1.56 | 2.4 | 1.72 | 1.72 | 2.6 | 1.88 | 1.88 | 2.8 | 2.04 | 2.04 | 3 | 2.2 | 2.2 | 3.2 | 2.36 | 2.36 | 3.4 | 2.52 | 2.52 | 3.6 | 2.68 | 2.68 | 3.8 | 2.84 | 2.84 | 4 | 3 | 3
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 5.1 | Filler and Inner sheath | Yes | Mandatory | The filler and inner sheath shall be of the following: a) Unvulcanized rubber, or b) Thermoplastic materiaIs, or c) Proofed tape ( for inner sheath only ). | Thermoplastic Material/ Unvulcanized rubber/ Proofed tape | Material : Filler and Inner Sheath | - | IS 1554-1 | - | - | - |  | 15.1 a) 4); Cl. 6.1.1 and 7.3.1 | Maximum resistance of conductor at 20 °C (Ω/km) Class 1 | [134 empty] | 36 | 36.7 | 24.5 | 24.8 | 18.1 | 18.2 | 12.1 | 12.2 | 18.1 | 7.41 | 7.56 | 12.1 | 4.61 | 4.7 | 7.41 | 3.08 | 3.11 | 4.61 | 1.83 | 1.84 | 4.61 | 1.15 | 1.16 | 1.91 | 0.727 | 3.08 | 0.524 | 0.868 | 0.387 | 0.641 | 0.268 | 0.443 | 0.193 | 0.32 | 0.153 | 0.253 | 0.124 | 0.206 | 0.164 | 0.125 | 0.1
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 5.2 | Filler and Inner sheath | No | Mandatory | Unvulcanized rubber or thermoplastic material used shall not be harder than PVC used for insulation (4.1) and for outer sheath (7.1). The materials shall be chosen to be compatible with temperature ratings of the cable and shall have no deleterious effect on any other component of the cable. | To be checked on declaration basis |  | - | - | - | - | - | No method has been given to determine the hardness | 15.1 a) 4); Cl. 6.2.3, 6.3.3 and 7.3.1 | Maximum resistance of conductor at 20 °C (Ω/km) Class 2 | [175 empty] | 18.1 | 18.2 |  | 12.1 | 12.2 | 18.1 | 7.41 | 7.56 | 12.1 | 4.61 | 4.7 | 7.41 | 3.08 | 3.11 | 4.61 | 1.83 | 1.84 | 3.08 | 1.15 | 1.16 | 1.91 | 0.727 | 0.734 | 1.2 | 0.524 | 0.529 | 0.868 | 0.387 | 0.391 | 0.641 | 0.268 | 0.27 | 0.443 | 0.193 | 0.195 | 0.32 | 0.153 | 0.154 | 0.253 | 0.124 | 0.126 | 0.206 | 0.0991 | 0.1 | 0.164 | 0.0754 | 0.0762 | 0.125 | 0.0601 | 0.0607 | 0.1 | 0.047 | 0.0475 | 0.0778 | 0.0366 | 0.0369 | 0.0605 | 0.0283 | 0.0286 | 0.0469 | 0.0221 | 0.0224 | 0.0367 | 0.0176 | 0.0177 | 0.0291 | 0.0151 | 0.0151 | 0.0247 | 0.0129 | 0.0129 | 0.0212 | 0.0113 | 0.0113 | 0.0186 | 0.0101 | 0.0101 | 0.0165 | 0.009 | 0.009 | 0.0149 | 0.0072 | 0.0072 | 0.0127
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 6.1 | Armouring | Yes | Mandatory | Armouring shall be of the following: a) Galvanized round steel wire, b) Galvanized steel strip, or c) Any metallic non-magnetic wire/strip. | Satisfactory/Unsatisfactory( a) Galvanized round steel wire, b) Galvanized steel strip, or c) Any metallic non-magnetic wire/strip.) To be checked on declaration basis | Declaration regarding type of Armouring is required | - | IS 1554-1 | - | - | - |  | 15.1 a) 4); Cl. 6.2.3, 6.3.3 and 7.3.1 | Minimum number of wires in the conductor (Class 2) | [259 empty] | 3 | 3 | 3 | 3 | 3 | 7 | 3 | 7 | 3 | 7 | 7 | 6 | 7 | 7 | 6 | 6 | 7 | 7 | 6 | 6 | 7 | 7 | 6 | 6 | 19 | 19 | 6 | 6 | 19 | 19 | 12 | 12 | 19 | 19 | 15 | 15 | 37 | 37 | 18 | 15 | 37 | 37 | 18 | 15 | 37 | 37 | 30 | 30 | 61 | 37 | 34 | 30 | 61 | 61 | 34 | 30 | 61 | 61 | 53 | 53 | 61 | 61 | 53 | 53 | 91 | 91 | 53 | 53 | 91 | 91 | 53 | 53 | 91 | 91 | 53 | 53
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 6.2 | Armouring | Yes | Mandatory | The galvanized steel wires/strips shall compIy with the requirements of IS : 3975-1979 | To be checked on declaration basis | Declaration regarding type of Armouring is required | - | IS 1554-1 | - | - | - | Referred IS 3975: 1979 has been put in the format | 15.1 a) 4); Cl. 6.4.3 and 7.3.1 | Maximum resistance of conductor at 20 °C (Ω/km) (Class 5) | [335 empty] | 39 | 40.1 | 26 | 26.7 | 19.5 | 20 | 13.3 | 13.7 | 7.98 | 8.21 | 4.95 | 5.09 | 3.3 | 3.39 | 1.91 | 1.95 | 1.21 | 1.24 | 0.78 | 0.795 | 0.554 | 0.565 | 0.386 | 0.393 | 0.272 | 0.277 | 0.206 | 0.21 | 0.161 | 0.164 | 0.129 | 0.132 | 0.106 | 0.108 | 0.0801 | 0.0817 | 0.0641 | 0.0654 | 0.0486 | 0.0495 | 0.0384 | 0.0391 | 0.0287 | 0.0292
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 6.2 | Armouring | Yes | Mandatory | The requirements of non-magnetic material shall be as agreed to between the purchaser and the supplier | To be checked on declaration basis | Declaration reagarding Requirements of non-magnetic material | - | IS 1554-1 | - | - | - | Referred IS 3975: 1979 has been put in the format | 15.1 a) 4); Cl. 6.4.3 and 7.3.1 | Maximum number of wires in the conductor (Class 5) | [379 empty] | 0.21 | 0.21 | 0.21 | 0.26 | 0.26 | 0.31 | 0.31 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.61 | 0.61
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 7.1.1 | Outer Sheath | Yes | Mandatory | For Cables with General Purpose InsuIafion - The outer sheath shall be of Type ST 1 PVC compound conforming to the requirements of IS : 5831-1984 | To be checked on declaration basis | Outer Sheath: For Cables with General Purpose Insulation, ST1 | 7.1.1 | IS 1554-1 | - | - | - | Referred IS 5831: 1979 has been put in the format | 15.1 a) 4); Cl. 6.4.3 and 7.3.1 | Maximum resistance of conductor at 20 °C (Ω/km) (Class 6) | [401 empty] | 39 | 40.1 | 26 | 26.7 | 19.5 | 20 | 13.3 | 13.7 | 7.98 | 8.21 | 4.95 | 5.09 | 3.3 | 3.39 | 1.91 | 1.95 | 1.21 | 1.24 | 0.78 | 0.795 | 0.554 | 0.565 | 0.386 | 0.393 | 0.272 | 0.277 | 0.206 | 0.21 | 0.161 | 0.164 | 0.129 | 0.132 | 0.106 | 0.108 | 0.0801 | 0.0817 | 0.0641 | 0.0654
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 7.1.2 | Outer Sheath | Yes | Mandatory | For Cables with Heat Resisting InsuIalion - The outer sheath shall be of Type ST 2 PVC compound conforming to the requirements of IS : 5831-1984* | To be checked on declaration basis | Outer Sheath: For Cables with Heat Resisting Insulation, ST2 | 7.1.2 | IS 1554-1 | - | - | - | Referred IS 5831: 1979 has been put in the format | 15.1 a) 4); Cl. 6.4.3 and 7.3.1 | Maximum diameter of wires in conductor (mm) (Class 6) | [439 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.41 | 0.41 | 0.41
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 7.1.3 | Outer Sheath | Yes | Mandatory | For cables with improved fire performance, the outer sheath shall, in addition, meet the requirement of tests applicable for the required category (see 15.1.1 and 15.2.1) | Satisfactory/Unsatisfactory (does not meet the requirement of tests applicable for the required category) | Outer Sheah: For cables with improved fire performance | - | IS 1554-1 | - | - | - |  | 15.1 a) 4); Cl. 6.5.3 and 7.3.1 | Maximum resistance of conductor at 20 °C (Ω/km) (Welding cables) | [458 empty] | 1.23 | 0.901 | 0.634 | 0.445 | 0.334 | 0.256
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 8.1 | Conductor | Yes | Mandatory | The construction of the conductor shall be as per the table | Solid/Stranded | CONSTRUCTION: Solid/Stranded | - | IS 8130-2013 | - | - | - |  | 15.1 a) 4); Cl. 6.5.3 and 7.3.1 | Maximum diameter of wires in conductor (mm) (Welding cables) | [464 empty] | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 8.1 | Conductor | Yes | Mandatory | The construction of the conductor shall be as per the table | Class1/Class 2 | CONSTRUCTION: Class1/Class 2 | - | IS 8130-2013 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 8.2 | Conductor | Yes | Mandatory | Cables with reduced neutral conductor shall have sizes as given in Table 1, (sqmm, nominal) | Value upto 0 decimal places, integer | CONSTRUCTION: Cable with Reduecd Neutral conductor, nominal cross sectional area of the main and neutral conductor | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 9.1 | Insulation | Yes | Mandatory | The conductor shall be provided with PVC insulation applied by extrusion. | To be checked on declaration basis | - | - | - | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 9.2 | Thickness of insulation | Yes | Mandatory | The average thickness of insulation shall be not less than the nominal value ( ii ) specified in Table 2 (mm, min) | Number of decimal places – Value upto 2 decimal places, integer | INSULATION:Thickness of Insulation |  | IS 10810: 1984 Part 6 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 9.3 | Tolerance on Thickness of Insulation | Yes | Mandatory | The smallest of the measured values of thickness of insulation shall not fall below the nominal value (ti in mm ) specified in Table 2 by more than 0.1 mm + 0.1 ti (mm, min) | Number of decimal places – Value upto 2 decimal places, whole number | INSULATION:Tolerance on Thickness of Insulation |  | IS 10810: 1984 Part 6 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 9.4 | Application of Insulation | Yes | Mandatory | The insulation shall be so applied that it fits closely on the conductor and it shall be possible to remove it without damage to the conductor. | Satisfactory/Unsatisfactory (does not fit closely on the conductor. Not possible to remove withoud damage to the conductor) |  | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.1 | Core identification | Yes | Mandatory | Cores shall be identified by different colouring of PVC insulation by adopting the scheme as per the clause. |  | No. of cores | - | IS 1554-1 | 1 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.1 | Core identification | Yes | Mandatory | 1 Core: red, black, yellow, blue or natural (non-pigmented) | Satisfactory/ Unsatisfactory (no. of cores and colour not matching) | No. of cores | - | IS 1554-1 | 2 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.1 | Core identification | Yes | Mandatory | 2 cores : red, yellow and blue | Satisfactory/ Unsatisfactory (no. of cores and colour not matching) | No. of cores | - | IS 1554-1 | 3 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.1 | Core identification | Yes | Mandatory | 3 cores : red, yellow and blue | Satisfactory/ Unsatisfactory (no. of cores and colour not matching) | No. of cores | - | IS 1554-1 | 4 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.1 | Core identification | Yes | Mandatory | 4 cores : red, yellow, blue, and black | Satisfactory/ Unsatisfactory (no. of cores and colour not matching) | No. of cores | - | IS 1554-1 | 5 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.1 | Core identification | Yes | Mandatory | 5 cores : red, yellow, blue, black and grey | Satisfactory/ Unsatisfactory (no. of cores and colour not matching) | No. of cores | - | IS 1554-1 | 6 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.1 | Core identification | Yes | Mandatory | 6 Cores and above : Two adjacent cores ( counting and direction core ) in each layer, blue and yellow, remaining cores grey, or in accordance with the scheme given in 10.3. | Satisfactory/ Unsatisfactory (no. of cores and colour not matching) | No. of cores | - | IS 1554-1 | 7 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.2 | Core identification | Yes | Mandatory | For reduced neutral conductors, the insulation colour shall be black. | Satisfactory/Unsatisfactory (the insulation colour is not black) | No. of cores | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.3 | Core identification | Yes | Mandatory | For cables having more than 5 cores, as an alternate to the provisions of 10.1, the core identification may be done by numbers. In that case, the insulation of cores shall be of the same colour and numbered sequentially, starting with number 1 for the inner layer. | Satisfactory/ Unsatisfactory (the insulation of cores is not of the same colour and not numbered sequentially) | No. of cores | - | IS 1554-1 | 1 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.3 | Core identification | Yes | Mandatory | The numbers shall be printed in Hindu-Arabic numerals on the outer surface of the cores. | Satisfactory/ Unsatisfactory (numbers not printed in Hindu-Arabic numerals on the outer surface of the cores/ not of the same colour) | No. of cores | - | IS 1554-1 | 2 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.3 | Core identification | Yes | Mandatory | All the numbers shall be of the same colour which shall contrast with the colour of the insulation. The numerals shall be legible | Satisfactory/ Unsatisfactory (numbers are of the same colour which shall contrast with the colour of the insulation. The numerals are not legible) | No. of cores | - | IS 1554-1 | 3 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 10.3.1 | Arrangement of Marking | Yes | Mandatory | The numbers shall be repeated at regular intervals along the core; consecutive numbers being inverted in relation to each other. When the number is a single numeral, a dash shall be placed underneath it. If the number consists of two numerals, these shall be disposed one below the other and a dash placed below the lower numeral. The spacing d between consecutive numbers shall not exceed 50 mm. The arrangemcnt of the marks Is shown in Fig. 1 | Satisfactory/ Unsatisfactory (arrangement of marks not as per Fig. 1) | CORE IDENTIFICATION:Arrangement of Marking | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 11.1 | Laying up of cores | Yes | Mandatory | In twin, three-and multi-core cables. the cores shall be laid up together with a suitable Lay; the outermost layer shall have right-hand lay and the successive layers shall be laid with opposite lay; where necessary, the interstices shall be tilled with non-hygroscopic material. | Satisfactory/Unsatisfactory (suitable lay not found) |  | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 11.2 | Laying up of cores | Yes | Mandatory | The recommended plan for lay-up of cores up to 100 is given in Table 3 | Satisfactory/ Unsatisfactory (lay-up of cores is not as per table 3) |  | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 12.1 | Inner Sheath | Yes | Mandatory | The laid up cores shall be provided with inner sheath either by extrusion or by wrapping. It shall be ensured that the shape is as circulat as possible | Satisfactory/Unsatisfactory (Inner sheath either by extrusion or by wrapping not found/ Circular shape not found) | Inner Sheath | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 12.2 | Inner Sheath | Yes | Mandatory | The inner sheath shall be so applied that it fits closely on the laid up cores and it shall be possible to remove it without damage to the insulation. | Satisfactory/Unsatisfactory ( does not fits closely on the laid up cores/ not possible to remove it without damage to the insulation) | Inner Sheath | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 12.3 | Thickness of Inner Sheath | Yes | Mandatory | The thickness of the inner sheath shall be as given in Table 4. Single core cables shall have no inner sheath.,(mm, min) | Thickness of inner sheath. Number of decimal places – Value upto 2 decimal places | INNER SHEATH :Thickness of Inner Sheath | - | IS 10462 (Part-1)-1983 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 13.1.1 | Armouring | Yes | Mandatory | Armouring shall be applied over the insulation in case of single core cables and over the inner sheath in case of twin-, three-and multicore cables | Satisfactory/Unsatisfactory (Armouring not provided) |  | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 13.1.2 | Armouring | Yes | Mandatory | The armour wires/formed wire shall be applied as closely as possible with a coverage of not less than 90 percent.(%, min) | Number of decimal places – Value upto 0 decimal places, whole no. or integer |  | - | IS 1554-1 |  | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 13.1.3 | Armouring | Yes | Mandatory | The direction of lay of the armour shall be left hand. For double wire/strip armoured cables, this requirement shall apply to the inner layer of wires/strips. The outer layer shall, except in special cases, be applied in the reverse the direction to the inner layer and there shall be a separator of suitable non-hygroscopic material, such as, plastic tape, bitumenized cotton tape, bitumenized hessian tape, rubber tape, proof tape, etc, between the layers of armour wires/strips. | Satisfactory/Unsatisfactory (direction of lay of | double wire/strip armoured | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 13.1.4 | Armouring | Yes | Mandatory | A binder tape may be provided on the armour. | Provided/not provided | - | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 13.2 | Type of Armour | Yes | Mandatory | Where the calculated diameter below armouring does not exceed 13 mm, the armour shall consist of galvanized round steel wires. Where the calculated diameter below armouring is greater than 13 mm, the armour shall consist of either galvanized round steel wires or galvanized steel strips. | a) Galvanized round steel wire, b) Galvanized steel strip, or c) Any metallic non-magnetic wire/strip. And the calculated diameter below armouring | a) Galvanized round steel wire, b) Galvanized steel strip, or c) Any metallic non-magnetic wire/strip. | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 13.2.1 | Type of Armour | Yes | Mandatory | In the case of single core cables intended for use on a.c. systems, the armouring shall be of non-magnetic materia | magnetic or non magentic material | armour: magnetic or non magentic material | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 13.3 | Dimensions | Yes | Mandatory | The dimensions of galvanized steel wires and strips shall be as specified in Table 5, mm | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Armouring : Dimensions -Wire Diameter | - | IS 10810: 1984 Part 36, IS 3975-1999 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 13.4 | Joints | Yes | Mandatory | The joints in armour wires/strips shall be made by brazing or welding and the surface irregularities shall be removed. A joint in any wire/strip shall be at least 300 mm from the nearest joint in any other wire/strip in the completed cable. (mm, min) | Number of decimal places – Value upto 1 decimal places, whole no. or integer | - | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 13.5.1 | Resistance | Yes | Optional | If specified by the purchaser, the d.c. resistance of the galvanized steel wire/strip armour shall be measured. The result, when corrected to 20 deg C, shall comply with the appropriate values given in Table 6, max, ohm/km) | Number of decimal places – Value upto 3 decimal places, whole no. or integer | test for DC resitance of the galvanised steel wire to be declared by the customer | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 13.5.2 | Resistance | Yes | Mandatory | In case of cables for use in mines, the resistance of armour shall not exceed that of the conductor as specified in IS : 8130-1984* by more than 33 percent. To satisfy this, substitution of galvanized steel wires/strips in armburing by the required number of tinned copper wires/ strips is permissible. (ohm/km, max) | Number of decimal places – Value upto 3 decimal places, whole no. or integer | ARMOURING : Resistance (For Mining Cable) | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 13.6 a) | Tensile strength | Yes | Mandatory | The tensile strength of round steel wire/formed steel wire shall be not less than 250 N/mm² and not more than 580 N/mm², min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | round steel wires/formed steel wire | - | IS 10810: 1984 Part 37 | 1 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 13.6 b) | Elongation | Yes | Mandatory | The elongation at break of round steel wire/formed steel wire shall be not less than 6 percent.(%, min) | Number of decimal places – Value upto 0 decimal places, whole no. or integer | round steel wires/formed steel wire | - | IS 10810: 1984 Part 37 | 2 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 13.6 c) | Torsion | Yes | Mandatory | Round steel wire shall meet the requirements of torsion test. The gauge length between vices and the minimum number of turns without break shall be as per Table 6 of IS 3975 : 1999 | Satisfactory/Unsatisfactory (Round steel wire does not meet the requirements of torsion test/ The gauge length between vices and the minimum number of turns without break is not as per Table 6 of IS 3975 : 1999) | round steel wires/formed steel wire | - | IS 10810: 1984 Part 38 | 3 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 13.6 d) | Zinc coating | Yes | Optional | The zinc coating shall not show any cracks and shall not flake off on rubbing by the bare finger when the formed steel wire is subjected to winding test. | Satisfactory/Unsatisfactory (Cracks/ Flakes observed) | round steel wires/formed steel wire | - | IS 10810: 1984 Part 39 | 4 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 13.6 e) | Uniformity of Zinc coating | Yes | Mandatory | The uniformity of zinc coating of round steel wire/formed steel wire shall comply with the requirements of IS 3975 : 1999 | Satisfactory/Unsatisfactory (uniformity of zinc coating does not comply as per IS 3975: 1999) | round steel wires/formed steel wire | - | IS 10810: 1984 Part 40 | 5 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 13.6 f) | Mass of zinc coating | Yes | Mandatory | The mass of zinc coating of round steel wire shall be not less than 95 percent of the mass specified in Table 2 of IS 4826 : 1979, g/m2, min | Mass of zinc coating, Number of decimal places – Value upto 2 decimal places | round steel wires/formed steel wire | - | IS 10810: 1984 Part 41 | 6 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 13.6 g) | Resistivity | Yes | Mandatory | The resistivity of the round steel wire/formed steel wire shall meet the requirements of IS 3975 : 1999, Mohm/cm, max | Number of decimal places – Value upto 1 decimal places, whole no. and integer | round steel wires/formed steel wire | - | IS 10810: 1984 Part 42 | 7 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 14.1 | Outer Sheath | Yes | Mandatory | The outer sheath shall be applied by extrusion. It shall be applied: a) over the insulation in case of unarmoured single-core cables; b) over the inner sheath in case of unarmoured twin, three-and multi-core cables; and c) over the armouring in case of armoured cables. | Satisfactory/Unsatisfactory (Outer sheath not found) | OUTER SHEATH | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 14.2 | Outer Sheath | Yes | Mandatory | The outer sheath shall be so applied that if fits closely over insulation inner sheath/armouring. It shall be possible to remove it without damage to the insulation/inner sheath. | Satisfactory/Unsatisfactory (does not fit closely on the conductor. Not possible to remove withoud damage to the conductor) | OUTER SHEATH | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 14.3 | Outer Sheath | Yes | Mandatory | The colour of the outer sheath shall be black, unless any other colour is agreed to between the purchaser and the supplier. | Black | OUTER SHEATH : Colour | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 14.4.1 | Unarmoured Cables | Yes | Mandatory | The average thickness of PVC outer Sheath of unarmoured cables shall be not less than the nominal value specified under co1 3 of Table 7 and the smallest of the measured values shall not be less than the minimum value specified in co1 4 of Table 7, mm , min | Number of decimal places – Value upto 2 decimal places, whole no. or integer | Thickness of Outer Sheath : Unarmoured Cables | - | IS 10462 (Part-1)-1983 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 14.4.2 | Armoured Cables | Yes | Mandatory | The thickness of outer sheath shall be not less than the minimum value specified in col 5 of Table 7, mm ,min | Number of decimal places – Value upto 2 decimal places, whole no. or integer | Thickness of Outer Sheath : Armoured Cables | - | IS 10462 (Part-1)-1983 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 a) 1) | Annealing test ( for copper ) Cl. 7.1.2.1 Before standing of IS 8130-2013 | Yes | Mandatory | Elongation shall not be less than the values given in the table, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Copper/Auminium conductors | - | IS 10810: 1984 Part 1 | 1 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 a) 2) | Tensile test Tests for Aluminium Conductors , Cl. 7.2.1 of IS 8130: 2013 | Yes | Mandatory | Before stranding — The tensile strength of any of the wires shall comply with the values given in 4.1, N/mm2, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Tensile test (for aluminium) - Before stranding | - | IS 10810: 1984 Part 2, IS 8130-2013 | 2 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 a) 2) | Tensile test Tests for Aluminium Conductors , Cl. 7.2.1 of IS 8130: 2013 | Yes | Mandatory | After stranding — The tensile strength of any of the wires shall be not less than 95 percent of the minimum values given in 4.1., N/mm2 | Number of decimal places – Value upto 1 decimal places, whole no. or integer | 0, H2, H4 Al Grade | - | IS 10810: 1984 Part 2, IS 8130-2013 | 3 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.1 a) 3) | Wrapping test ( for aluminium 1, Cl. 7.2.2 of IS 8130: 2013 | Yes | Mandatory | The wire shall not break | Did not break/ break | Copper/Auminium conductors | - | IS 10810: 1984 Part 3 | 4 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 a) 4) | Cl. 7.3.1 Resistance Test (for Both Copper and Aluminium) of IS 8130: 3013 | Yes | Mandatory | The corrected dc resistance shall not exceed the values given in the appropriate Table 1 to Table 5. ohm/km | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Copper(Plain or tinned)/Auminium conductors, Nomina cross sectional area | - | IS 10810: 1984 Part 5 | 5 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 b) | Test for armouring wires/strips | Yes | Mandatory | Wire, upto and including 1.60 mm, Tensile strength 300-500 Mpa, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Armour, wire, formed wire or tape | - | IS 10810 (Part 7) | 6 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 b) | Test for armouring wires/strips | Yes | Mandatory | Wire, over Tensile strength 1.60 mm, 300-500 Mpa, Mpa, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Armour, wire, formed wire or tape | - | IS 10810 (Part 7) | 7 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 b) | Test for armouring wires/strips | Yes | Mandatory | Formed wire, Tensile strength 300-500 Mpa, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Armour, wire, formed wire or tape | - | IS 10810 (Part 7) | 8 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 b) | Test for armouring wires/strips | Yes | Mandatory | Tape, Tensile strength 300-450 Mpa, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Armour, wire, formed wire or tape | - | IS 10810 (Part 7) | 9 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 b) | Test for armouring wires/strips | Yes | Mandatory | Wire, upto and including 1.60 mm, Min percentage elongation : 10% | percentage elongation, Number of decimal places – Value upto 0 decimal places | Armour, wire, formed wire or tape | - | IS 10810 (Part 7) | 10 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 b) | Test for armouring wires/strips | Yes | Mandatory | Wire, over 1.60 mm, Min percentage elongation : 10 | percentage elongation, Number of decimal places – Value upto 0 decimal places, whole no. or integer | Armour, wire, formed wire or tape | - | IS 10810 (Part 7) | 11 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 b) | Test for armouring wires/strips | Yes | Mandatory | Formed wire, M,in percentage elongation : 10 % | percentage elongation, Number of decimal places – Value upto 0 decimal places | Armour, wire, formed wire or tape | - | IS 10810 (Part 7) | 12 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 b) | Test for armouring wires/strips | Yes | Mandatory | Tape, Min percentage elongation : 10 % | percentage elongation, Number of decimal places – Value upto 0 decimal places, whole no. or integer | Armour, wire, formed wire or tape | - | IS 10810 (Part 7) | 13 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 c) | Test for thickness of insulation and sheath | Yes | Mandatory | 9,12,14, Table 2, Table 4 and Table 7 | Satisfactory/Unsatisfactory (failed in thickness of insulation/ failled in thickness of sheath) | - |  | IS 10810: 1984 Part 6 | 14 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)1) | Insulation, Tensile Strength at break (without ageing) | Yes | Mandatory | Type A-12.5 N/mm2, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of insulation | - | IS 10810: 1984 Part 7 | 15 | - | - | The method has been defined in IS 10810 (column P) and the values have been defined in IS 5831 (Column Q)
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)1) | Insulation, Tensile Strength at break (without ageing) | Yes | Mandatory | Type C-12.5 N/mm2, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of insulation | - | IS 10810: 1984 Part 7 | 16 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)2) | Insulation, elongation at break (without ageing) | Yes | Mandatory | Type A- 150, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of insulation | - | IS 10810: 1984 Part 11 | 17 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)2) | Insulation, elongation at break (without ageing) | Yes | Mandatory | Type C- 125, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of insulation | - | IS 10810: 1984 Part 11 | 18 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)1) | Sheath, Tensile Strength at break (without ageing) | Yes | Mandatory | ST1- 12’5, N/mm2, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 7 | 19 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)1) | Sheath, Tensile Strength at break (without ageing) | Yes | Mandatory | ST2-12’5, N/mm2, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 7 | 20 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)2) | Sheath, elongation at break (without ageing) | Yes | Mandatory | ST1-150, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 11 | 21 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)2) | Sheath, elongation at break (without ageing) | Yes | Mandatory | ST2-150, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 11 | 22 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)1) | Insulation, Tensile Strength at break (with ageing) | Yes | Mandatory | Type A, tensile -12’5 | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 7 | 23 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)1) | Insulation, Tensile Strength at break (with ageing) | Yes | Mandatory | Type C, tensile -12’5 | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 7 | 24 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)1) | Insulation, Tensile Strength at break (with ageing) | Yes | Mandatory | Type A, Variation, -+ 20 | Number of decimal places – Value upto 0 decimal places | Type of insulation | - | IS 10810: 1984 Part 7 | 25 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)1) | Insulation, Tensile Strength at break (with ageing) | Yes | Mandatory | Type C, Variation, -+ 25 | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of insulation | - | IS 10810: 1984 Part 7 | 26 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)2) | Insulation, elongation at break (with ageing) | Yes | Mandatory | Type A, -150, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of insulation | - | IS 10810: 1984 Part 11 | 27 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)2) | Insulation, elongation at break (with ageing) | Yes | Mandatory | Type C-125, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of insulation | - | IS 10810: 1984 Part 11 | 28 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)1) | Sheath, Tensile Strength at break (with ageing) | Yes | Mandatory | ST1, tensile and variation-12.5 | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 7 | 29 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)1) | Sheath, Tensile Strength at break (with ageing) | Yes | Mandatory | ST2, tensile and variation-12.5 | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 7 | 30 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)2) | Sheath, elongation at break (with ageing) | Yes | Mandatory | ST1, Elongation -12.5, %, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 11 | 31 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)2) | Sheath, elongation at break (with ageing) | Yes | Mandatory | ST2, Elongation -12.5, %, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 11 | 32 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)2) | Sheath, elongation at break (with ageing) | Yes | Mandatory | ST1,variation-+ 20 %, max | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 11 | 33 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)2) | Sheath, elongation at break (with ageing) | Yes | Mandatory | ST2, variation-+ 25 %, max | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of Sheath | - | IS 10810: 1984 Part 11 | 34 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)3) | Shrinkage test-Treatment | Yes | Mandatory | Type-A-150, %, min Type-C- %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 12 | 35 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)3) | Shrinkage test- | Yes | Mandatory | Type-A-4 %, min Type-C-4, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 12 | 36 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)3) | Sheath- Shrinkage | Yes | Mandatory | ST1- 04, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of sheath | - | IS 10810: 1984 Part 12 | 37 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)3) | Sheath- Shrinkage | Yes | Mandatory | ST2-04, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of sheath | - | IS 10810: 1984 Part 12 | 38 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)4) | Hot deformation test-Depth of indentation | Yes | Mandatory | Type A-50, %, min Type C -50, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 15 | 39 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)4) | Sheath -Depth of indentation | Yes | Mandatory | ST1-50, %, min ST2-50, %, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of sheath | - | IS 10810: 1984 Part 15 | 40 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)5) | Sheath -Depth of indentation | Yes | Mandatory | ST1-02, mg/sqcm ST2-02, mg/sqcm | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of sheath | - | IS 10810: 1984 Part 10 | 41 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.1 d)6) | Insulation- Heat shock test-Visual examination | Yes | Mandatory | No signs of cracks or scales | Satisfactory/Unsatisfactory (cracks/scales observed) | Heat shock test- Insulation | - | IS 10810: 1984 Part 14 | 42 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.1 d)6) | Sheath- Heat shock test-Visual examination | Yes | Mandatory | No signs of cracks or scales | Satisfactory/Unsatisfactory (cracks/scales observed) | Heat shock test- sheath | - | IS 10810: 1984 Part 14 | 43 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)7) | Thermal stability- insulation- Time | Yes | Mandatory | Type A-80, minutes, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 60 | 44 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 d)7) | Thermal stability- insulation- Time | Yes | Mandatory | Type C-100, minutes, min | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 60 | 45 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 e) | Volume resistivity- at maximum rated temperature | Yes | Mandatory | Type A- 1 x 10^10, Ohm-cm, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 43 | 46 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 e) | Volume resistivity- at 27 deg C | Yes | Mandatory | Type A- 1 x 10^3, Ohm-cm, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 60 | 47 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 e) | Volume resistivity- at maximum rated temperature | Yes | Mandatory | Type C- 1x 10^10, Ohm-cm, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 43 | 48 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 e) | Volume resistivity- at 27 deg C | Yes | Mandatory | Type C- 1x 10^13, Ohm-cm, min | Number of decimal places – Value upto 1 decimal places, whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 43 | 49 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 e) | Insulation resistance constant,-at maximum rated temperature | Yes | Mandatory | Type A-0.037, Megaohm-km | Number of decimal places – Value upto 3 decimal places,, , whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 43 | 50 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1 e) | Insulation resistance constant,-at maximum rated temperature | Yes | Mandatory | Type C -0.037, Megaohm-km | Number of decimal places – Value upto 3 decimal places, , whole no. or integer | Type of Insulation | - | IS 10810: 1984 Part 43 | 51 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.1 f), 16.3.1, | High Voltage Test ( Water Immersion Test )- A.C Test | Yes | Mandatory | The core or cores ( not exceeding five cores in the case of multicore cables ) shall be carefully removed from a sample approximately 3 m long taken from the finished cable. They shall be immersed in water bath that their ends protrude at least 200 mm above the water level. The temperature of the water bath shall be 60+-3 deg C for cores with general purpose PVC insulation and 70+-3 deg C for cores with heat resisting PVC insulation. After 24 hours, a voltage of 3 kV ( rms ) shall be applied between the conductors and water. This voltage shall be raised to 6 kV ( rms ) within 10 seconds and held constant at this value for 5 minutes. If the sample fails in this test, one more sample shall be subjected to this test. There shall be no failure in the repeat test. | Satisfactory/Unsatisfactory (cannot withstand the test) | - | - | IS 10810: 1984 Part 45 | 52 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.1 f),, 16.3.2 | High Voltage Test ( Water Immersion Test )- D.C Test | Yes | Mandatory | The cores which have passed the preliminary test in 16.3.1 shall be subsequently tested with a d.c. voltage of 1’2 kV in the same water bath at the same temperature. The core shall withstand this voltage for 240 hours without breakdown. | Satisfactory or Unsatisfactory (cannot withstand the test) | - | - | IS 10810: 1984 Part 45 | 53 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.1 g),16.2 | High Voltage Test at Room Temperature - | Yes | Mandatory | The cable shall withstand an a.c. voltage of 3 kV ( rms ) or a dc voltage of 7’2 kV. The duration of test shall be 5 minutes for each connection | Satisfactory or Unsatisfactory (cannot withstand the test) | - | - | IS 10810: 1984 Part 45 | 54 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1.1 a),16.5 | Sheath - Oxygen index | Yes | Mandatory | The test on samples of inner/outer sheath (as applicable) shall be done at 27 ~ 2°C. The oxygen index shall not be less than 29 | Oxygen index, Number of decimal places – Value upto 0 decimal places | Category C1/C2: Oxygen index Test | - | IS 10810: 1984 Part 58 | 55 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.1.1 b), 16.6 | Flame Retardance Test on Single Cables | Yes | Mandatory | After the test there should be no visible damages on the test specimen within 300 mm from its upper end. Marks from fixing devices, soot or changing of the colour are not considered damages | Satitsfactory/ Unsatisfactory (damage observed) | Category C1/C2: Flame retardance test on Single cable | - | IS 10810: 1984 Part 61 | 56 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.1.1 c),16.7 | Flame Retardance Test on Bunched Cables | Yes | Mandatory | After burning has ceased, the cables should be wiped clean and the charred or affected portion should not have reached a height exceeding 2.5 m above the bottom edge of the burner, measured at the front and rear of the cable assembly. | Satitsfactory/ Unsatisfactory (Charred position exceed the limit) | Category C1/C2: Flame retardance test on bunched Cable cable | - | IS 10810: 1984 Part 62 | 57 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1.1 d),16.10 | Test for Temperature Index | Yes | Mandatory | The measured value of Temperature index, number | Number of decimal places – Value upto 0 decimal places, whole no. | Category C1/C2: Temperature Index | - | IS 10810: 1984 Part 58 | 58 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1.1 e) | Smoke Density | Yes | Mandatory | Under consideration. | - | - | - | - | 59 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.1.1 f), 16.9 | Test for Halogen Acid Gas Evolution | Yes | Mandatory | The level of HCI evolved shall not exceed 20 percent by weight., max, % | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Category C2: Halogen acid gas Evolution Test | - | IS 10810: 1984 Part 59 | 60 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.4 a) | Insulation- Cold bend test-Visual examination | Yes | Mandatory | No signs of cracks or scales | Satisfactory/Unsatisfactory(craks or scales observed) | Declaration required regardig applicability of Cold bend test- Insulation ( Optional test) | - | IS 5831 | 61 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.4 a) | Sheath- Cold bend test-Visual examination | Yes | Optional | No signs of cracks or scales | Satisfactory/Unsatisfactory(craks or scales observed) | Declaration required regardig applicability of optional test Cold bend test- Sheath ( Optional test) | - | IS 5831 | 62 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.4 b) | Insulation-Cold impact test-Visual examination | Yes | Optional | No signs of cracks or scales | Satisfactory/Unsatisfactory(craks or scales observed) | Declaration required regardig applicability of Cold impact test- Insulation ( Optional test) | - | IS 5831 | 63 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 15.4 b) | Sheath- Cold impact test-Visual examination | Yes | Optional | No signs of cracks or scales | Satisfactory/Unsatisfactory(craks or scales observed) | Declaration required regardig applicability of Cold impact test- Sheath ( Optional test) | - | IS 5831 | 64 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 15.3 c) | Routine Tests-Armour resistance test | Yes | Optional | Armour resistance in ohm, max | Number of decimal places – Value upto 0 decimal places, whole no. or integer | Armour resistance test ( for other than mining cables ).- Optional test | - | IS 5831 | 65 | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Quantitative | 16.4 | Flammability Test | Yes | Mandatory | Period of burning after removal of the flame shall not exceed 60 seconds and the unaffected ( uncharred ) portion from the lower edge of the top clamp shall be at least 50 mm. | Period of burning ( Sec)/Unaffected Portion (mm), Number of decimal places – Value upto 0 decimal places | - | - | IS 10810: 1984 Part 53 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 17.1 | Manufacturer’s Identification | Yes | Mandatory | The manufacturer shall be identified throughout the length of the cable by means of a tape bearing the manufacturer’s name or trade-mark, or by manufacturer’s name or trade-mark being indented, printed or embossed on the cable. In case none of these methods can be employed, or if the purchaser so desires, colour identification threads in accordance with a scheme to be approved by the Bureau of Indian Standards shall be employed. The indentation, printing or embossing shall be done only on the outer sheath. | Satisfactory/ Unsatisfactory (Not marked) | - | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 17.2 | Cable Identification | Yes | Mandatory | In order to distinguish these electric cables from telephone cables, the word ‘ELECTRIC’ shall be indented, printed or embossed throughout the length of the cable. In case of cables intended for use in mines, the word ‘MINING’ also shall be indented, printed or embossed throughout the length of the cable. The indentation, printing or embossing shall be done only on the outer sheath. | Satisfactory/ Unsatisfactory (Not marked) | - | - | IS 1554-1 | - | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 17.2.1,17.2.2 | Cable Identification | Yes | Mandatory | Cables with heat resisting insulation suitable for 85’C conductor temperature shall be identified by the letters ‘HR 85’ marked on it in any of the manner specified in 17.2. | Satisfactory/ Unsatisfactory (HR 85/FR/FR-LSH not marked) | - | - | IS 1554-1 |  | - | -
IS 1554 | 1 | N.A. | 1988 | 5 | PVC INSULATED HEAVY DUTY ELECTRIC CABLE , PART 1 (For working voltage up to and including 1100V) | Electrical | Qualitative | 17.3 | Cable Code | Yes | Mandatory | Cable Code | Satisfactory/ Unsatisfactory (Not marked) | - | - | IS 1554-1 | - | - | -

## Test Request Format
Annex-D
TEST REQUEST FORMAT
Class of Conductor | Nominal Cross-section area of conductor/Nos of Core | Conductor | Conductor Shape | Type of Insulation | Type of Sheath | Category of Cable | Armouring | Armour type | Grade of Aluminium | Cable Identification | Cable Code | Requirement of Non-Magnetic material | Optional test | No. of Cores
Class 1/Class 2 | Nominal Cross-section area of conductor/Core | Plain Copper/ Tinned Copper/ Aluminium | Solid/Circular/Circular Compacted/Shaped | Type A/Type C | Type ST1/ST2 | 01/C1/C2 | Armoured/Unarmoured | Galvznised round steel wire/ Galvanised steel strip/ Metallic Magnetic/Non Magnetic wire/strip | O/H2/H4 | (ELECTRIC/MINING) Declared by manufacturer | Declared by manufacturer | To be specified by the Manufacturer | Cold bend test, Cold impact test, Armour resistance test (for m ining cables) | 1,2,3,4,5,6 and above